#### VZ.TPR.9211 Vendor Power and Grounding Questionnaire

Data Sheet

##### Equipment Powering

  - Is your equipment powered through an “A” and “B” fuses?

Yes:  Equipment is either Duplex, OR’d, or Logic OR’d powered (go on to Question 2)

No:   Equipment is Simplex power (Skip Question 2, 3 & 4)

  - If an upstream (i.e. external) fuse feeding “A” blows does the current double in / transfer to fuse “B”?

Yes:  Equipment is OR’d or Logic OR’d or Parallel Fused    (go on to Question 3)

No:   Equipment is Duplex powered (Skip Questions 3 & 4)

N/A:  Answer to Question 1 was “No”

  - If the upstream (i.e., external) fuse that powers the “A” side blows, can you read voltage (–48 nominal) on the equipment side (downstream) of the blown fuse?

Yes:  Equipment has Parallel Fusing (NEC Violation-skip question 4).

No:    Equipment is either OR’d or Logic OR’d powered (got to question 4).

N/A:  Answer to Question 1 was “No” or answer to Question 2 was B or N/A

  - In a normal (no fault) condition is current through fuse “A” and through fuse “B” substantially equal?

Yes:   Equipment is OR’d powered

No:     Equipment is Logic OR’d powered

N/A:    Answer to Question 1 was “No”, or answer to Question 2 was “No” or N/A, or answer to question 3 was either “Yes” or N/A.

| Question | Response (Yes, No, or N/A) |
| --- | --- |
| 1: Is your equipment fed by an “A” and “B” fuses? |  |
| 2: If fuse “A” blows, does the current double in / transfer to in fuse “B”? |  |
| 3: If fuse “A” blows, can you read voltage (–48 nominal) on the equipment side (downstream) of the blown fuse? |  |
| 4: In normal (no fault) condition is current through fuse “A” and through fuse “B” substantially equal? |  |

Format for the Vendor Response

Operational DC Voltage

What are the maximum, minimum, and nominal operational DC voltages and associated DC current for the subject equipment?  Consider the equipment to be fully loaded with a full compliment of cards, etc.  For equipment with a variety of cards, assume the equipment is fully loaded with cards having the largest current draw.  For the purposes of this questionnaire, the voltage and currents requested are per external power bus feeds as measured at the external input to the equipment.  If the “A” side draws 35 amps and the “B” side draws 42 amps then record “35” and “42” in the appropriate columns.

The maximum voltage is the highest level voltage the equipment can tolerate without damage.  This question is to ensure the equipment will operate within the conventional battery float/equalize voltage ranges.

The Minimum Voltage is the voltage at which the equipment internal power converters shut down and no longer draw current from the external power bus; the current is the maximum current drawn just prior to the converters going off-line.

Note: When inputting the values for current, consider the A & B power bus and subject equipment to be in a “No Fault” state: the equipment is operating normally and no supply fuses are blown.

For Logic OR’d equipment, assume the “A” power bus is the active bus.  Enter the current drawn by both “A” and “B” sides when “A” is active.  If the readings are different when “B” power bus is active, enter the readings with the largest current draw.  Specify the logic circuit hysteresis voltage.  The switching time from the active bus to the inactive bus is the time required for the logic circuit to determine that the inactive bus is the “best source” then switch from either “A” to “B” or from “B” to “A”.  Enter switching time in engineering units (i.e., ms or μs).

|  | “A” Feed Volts | “A” Feed Amps | “B” Feed Volts | “B” Feed Amps |
| --- | --- | --- | --- | --- |
| Maximum operating voltage |  |  |  |  |
| 48 volts nominal | 48.0 |  | 48.0 |  |
| 42.0 volts | 42.0 |  | 42.0 |  |
| Minimum Voltage (power converters shut down) |  |  |  |  |

Format for the Vendor Response

Logic OR’d Power Only

|  | “A” to “B” | “B” to “A” |
| --- | --- | --- |
| Switching time from active bus to inactive bus |  |  |
| Logic circuit hysteresis (volts) |  |  |

Format for the Vendor Response

Grounding

There are three components that are a factor in how a piece of equipment is installed and protected in a central office environment.  By using the following definitions and referencing them to your equipment, Verizon can properly install and maintain them to their peak of reliability.

I. Equipment Frame: 	Single Point Ground or Common Bonded Network?

# II. Logic: 		Referenced to Chassis or Referenced to Power Return?

III. Power Ground: 	Integrated Power or Isolated Power?

| Question | Response |
| --- | --- |
| Equipment Frame |  |
| Logic |  |
| Power Ground |  |

Format for the Vendor Response

Connector Types

Threaded Pressure Mechanical Connectors

For each external power input designed for threaded pressure mechanical connectors, define the maximum current drawn and the required torque to connect the external power cable to the equipment.  Verizon standard IP 72202 and Verizon practice VZ 292-100-000 place limitations on the type of power connectors used in central offices.  Specifically, threaded pressure mechanical connectors are limited to wire sizes less than #14 AWG.

| External power input information | Number of external power inputs | Maximum fully loaded current at -48 volts | Mechanical connector torque (in/lbs) | Manufacturer recommended wire size (# AWG) |
| --- | --- | --- | --- | --- |
| -48 volt supply |  |  |  |  |
| -48 volts return |  |  |  |  |

Format for the Vendor Response

Compression Connectors

For each external power source that terminates on the equipment that is designed for compression connectors, define the minimum and maximum cable lug for the equipment.  Note that each external power and power return cable compression lug connection requires a two-hole lug and requires a physical barrier between each lug landing location. Lugs shall not touch and the inspection window shall be visible after installation. Lugs shall be standard off the shelf (no special order) American sizes (i.e., not metric) with standard NEMA spacing such as a ¼” bolt with 5/8” centers, a 3/8” bolt with 1” center, and a 1/2” bolt with 1-3/4” centers.  Use NEC table 310-16 at 75°C when calculating cable currents and required cable lugs.  Note that due to Verizon defined maximum allowable voltage drops between a power source and the equipment, the lug landings should be sized to allow the lug size determined by maximum current draw plus the next two larger sized lugs.  For example, if the maximum current draw requires a #10 AWG cable and lug, the lug landing should be sized to accept up to a #6 AWG lug.

| External power input and lug information | Number of external power inputs | Two-hole (Yes/No) | Minimum lug size | Maximum lug size |
| --- | --- | --- | --- | --- |
| -48 volt supply |  |  |  |  |
| -48 volts return |  |  |  |  |

Format for the Vendor Response

# Over Current Protection

The following questions are used to determine maximum cable size and to verify fuse and circuit breaker coordination in accordance with Verizon Practice 292-100-000.

For each external power input to the equipment, identify the type and current rating of any over current (OC) protective device embedded as part of the equipment chassis.  Note that Telecom DC power distribution fuses are the only fuses authorized by Verizon.  Enter N/A if there is no embedded over current protective device.

The fuse rating is the current at which the fuse will open.  The circuit breaker rating is the current rating on the front of the breaker, usually on the switch arm.  The circuit breaker trip setting is the current at which the breaker will trip.  The trip setting of a breaker is 125% of the circuit breaker rating.  For example, a 60-amp breaker (as labeled on the front of the breaker) will trip at 75 amps.

| OC Protective Device | Type of Fuse | Fuse Rating | Breaker Rating | Breaker Trip setting |
| --- | --- | --- | --- | --- |
| Fuse |  |  |  |  |
| Breaker |  |  |  |  |

Format for the Vendor Response

Fuse type examples include GMT, TPN, TPL, TPH, TPC, and TPW.

#### REPORTING REQUIREMENTS

Complete all tables herein and provide a copy along with the NEBS test report submission to Verizon’s NEBS, Fiber and Energy Efficiency Group.