TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

PART 11

LIGHTNING AND POWER FAULT

Section 4, GR-1089-CORE

Telcordia Technologies GR-1089, Issue 6, May 2011

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Test Results Summary	3

Overview	7

Overview (4.1)	8

Current-Limiting Protectors (4.2.2)	9

Test Equipment (4.5.1)	10

Equipment Interfacing With Agreed or Non-Field Replaceable Integrated Primary Protectors (4.5.9)	11

Short Circuit Test (Telecommunications Type 1, 3, and 5 Ports) (4.6.1.1)	12

Ethernet Interface Considerations (Telecommunications Type 1, 2, 3, 3a/5a, 3b/5b, 4, 4A, or 5 ports. (4.6.1.2)	13

Cell Site Inter-Structure Withstand Criteria (Telecommunications Type 3a/5a and 8b ports. (4.6.1.3)	14

First-Level Lightning Criteria for Telecommunications Ports (Type 1, 3, 3b/5b, and 5 ports) (4.6.2.1.1)	15

Intra-Building or Intra-Site Lightning Criteria (Telecommunications Type 2, 3a/5a, 4, 4a ports. (4.6.2.1.3)	17

First-Level Lightning Criteria for Antenna Ports (Telecommunications Type 6 Ports) (4.6.2.1.5)	21

First-Level Lightning Criteria for AC Power Ports (Telecommunications Type 7 Ports) (4.6.2.1.6)	22

DC Power to Antenna Lightning Criteria (Type 8a Ports) (4.6.2.1.7)	25

Second-Level Lightning for Telecommunication Ports (Type 1, 3, and 5 Ports) (4.6.3.1)	26

Second-Level Lightning for AC Power Ports (Type 7 Ports) (4.6.3.2)	27

First-Level Power Fault/Induction Requirements (4.6.4.1)	28

Second-Level Power Fault Requirements (4.6.4.2)	30

Criteria for Equipment With Integrated Primary Protection (4.7)	33

Equipment Classification (4.7.1)	34

Protector Requirements (4.7.2)	36

Lightning Surge and Power Fault Tests for Protected Circuits (4.7.3)	39

Fusing Coordination for Circuits That Contain Components or Circuitry That Act as osp fuse links (4.7.4.1)	41

Enclosure Suitable for Fusing (4.7.4.1.1)	77

Fusing Coordination for Circuits Not Containing Components or Circuitry That Act as osp fuse links (4.7.4.2)	78

Dielectric Withstand (4.7.5)	80

EIPP Cable Requirements (4.7.6)	81

AC Power Fault Immunity — Unprotected Circuits (4.7.7)	83

Lightning Surge Tests — Unprotected Circuits (4.7.8)	84

Lightning Surge Tests for Severe Climatic Conditions — Unprotected Units (4.7.8.1)	85

Lightning Protection Tests for Equipment To Be Located in High- Exposure Customer Premises and OSP Facilities (Type 3 and 5 Telecommunications Ports) (4.7)	86

Criteria for Equipment Interfacing With Agreed Primary Protection (4.8)	88

Appendix A	92

## Test Results Summary

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results.>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-1089-CORE.

- Section Name column gives the Section name from GR-1089-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-1089-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, Non-compliant, etc.).

- Compliant: The Equipment Under Test met the requirements of the corresponding criteria.

- Non-compliant: The Equipment Under Test did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to Equipment Under Test {Explanation Required}

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- Page column gives the page number, in this report, for the corresponding criteria.

Table 11-1: Lightning and AC Power Fault Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Comments | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 4 | Lightning and AC Power Fault | - |  |  | - |
| 4.1 | Overview | R4-1 [231] |  |  | 8 |
| 4.2.2 | Current-Limiting Protectors | R4-2 [232] |  |  | 9 |
| 4.5.1 | Test Equipment | R4-3 [26] |  |  | 10 |
| 4.5.9 | Equipment Interfacing With Agreed or Non-Field Replaceable Integrated Primary Protectors | R4-4 [179] |  |  | 11 |
|  |  | R4-5 [181] |  |  |  |
| 4.6.1.1 | Short Circuit Test (Telecommunications Type 1,3, and 5 Ports) | R4-6 [25] |  |  | 12 |
| 4.6.1.2 | Ethernet Interface Considerations (Telecommunications Type 1 ,2 ,3 , 3a/5a , 3b/5b, 4,4a, or 5 Ports) | R4-7 [233] |  |  | 13 |
| 4.6.1.3 | Cell Site Inter-Structure Withstand Criteria (Telecommunications Type 3a/5a and 8b Ports) | R4-8 [234] |  |  | 14 |
| 4.6.1.3.2 | Option B – Surge Test | CR4-9 [235] |  |  | 15 |
| 4.6.2.1.1 | First-Level Lightning Criteria for Telecommunications Ports (Type 1, 3, 3b/5b, and 5 ports) | R4-10 [27] |  |  | 16 |
|  |  | R4-11 [167] |  |  |  |
|  |  | R4-12 [236] |  |  |  |
| 4.6.2.1.2.7 | Test Procedure ad Criteria for Surge Test Number 7 of Table 4-2 – High Lightning Exposure Test for Remote OSP Interfaces | CO4-13 [178] |  |  | 17 |
| 4.6.2.1.3 | Intra-Building or Intra-Site Lightning Criteria (Telecommunications Type 2, 3a/5a, 4, 4a Ports) | R4-14 [30] |  |  | 18 |
|  |  | R4-15 [169] |  |  |  |
|  |  | R4-16 [31] |  |  |  |
|  |  | R4-17 [170] |  |  |  |
|  |  | R4-18 [237] |  |  |  |
| 4.6.2.1.5 | First-Level Lightning Criteria for Antenna Ports (Telecommunications Type 6 ports) | R4-19 [209] |  |  | 20 |
|  |  | R4-20 [238] |  |  |  |
| 4.6.2.1.6 | First-Level Lightning Criteria for AC Power Ports (Telecommunications type 7 ports) | R4-21 [210] |  |  | 21 |
|  |  | R4-22 [32] |  |  |  |
|  |  | R4-23 [211] |  |  |  |
|  |  | R4-24 [239] |  |  |  |
| 4.6.2.1.7 | DC Power to Antenna Lightning Criteria (Type 8a Ports) | R4-25 [240] |  |  | 23 |
| 4.6.3.1 | Second-Level Lightning for Telecommunications Ports (Type 1, 3, and 5 ports) | R4-26 [29] |  |  | 26 |
|  |  | R4-27 [241] |  |  |  |
| 4.6.3.2 | Second-Level Lightning for AC Power Ports (Type 7 ports) | R4-28 [33] |  |  | 27 |
|  |  | R4-29 [242] |  |  |  |
| 4.6.4.1 | First-Level Power Fault/Indication Requirements | R4-30 [35] |  |  | 28 |
|  |  | R4-31 [172] |  |  |  |
|  |  | R4-32 [173] |  |  |  |
| 4.6.4.2 | Second-Level Power Fault Requirements | R4-33 [40] |  |  | 30 |
|  |  | R4-34 [41] |  |  |  |
|  |  | R4-35 [36] |  |  |  |
|  |  | R4-36 [174] |  |  |  |
|  |  | R4-37 [175] |  |  |  |
| 4.7 | Criteria for Equipment With Integrated Primary Protection | R4-38 [182] |  |  | 32 |
| 4.7.1 | Equipment Classification | R4-39 [183] |  |  | 33 |
|  |  | R4-40 [184] |  |  |  |
| 4.7.2 | Protector Requirements | R4-41 [185] |  |  | 35 |
|  |  | R4-42 [186] |  |  |  |
|  |  | R4-43 [187] |  |  |  |
|  |  | R4-44 [188] |  |  |  |
|  |  | R4-45 [189] |  |  |  |
|  |  | R4-46 [190] |  |  |  |
| 4.7.3 | Lightning Surge and power Fault Tests for Protected Circuits | R4-47 [191] |  |  | 37 |
| 4.7.4.1 | Fusing Coordination for Circuits That Contain Components or Circuitry That Act as OSP Fuse links | R4-48 [193] |  |  | 38 |
| 4.7.4.1.1 | Enclosure Suitable for Fusing | R4-49 [194] |  |  | 39 |
|  |  | R4-50 [195] |  |  |  |
|  |  | R4-51 [196] |  |  |  |
| 4.7.4.2 | Fusing Coordination for Circuits Not Containing Components or Circuitry That Act as OSP Fuse links | R4-52 [199] |  |  | 40 |
| 4.7.5 | Dielectric Withstand | R4-53 [200] |  |  | 42 |
| 4.7.6 | EIPP Cable Requirements | R4-54 [201] |  |  | 43 |
|  |  | R4-55 [202] |  |  | 43 |
| 4.7.7 | AC Power Fault Immunity – Unprotected Circuits | R4-56 [203] |  |  | 44 |
| 4.7.8 | Lightning Surge Tests – Unprotected Circuits | R4-57 [204] |  |  | 45 |
| 4.7.8.1 | Lightning Surge Tests for Severe Climatic Conditions – Unprotected Units | CR4-58 [205] |  |  | 47 |
|  |  | CR4-59 [206] |  |  |  |

## Overview

### Project Objective

Testing was performed to determine if the <Product Name> met the requirements for Section 4, Lightning and AC Power Fault, of Telcordia Technologies GR-1089-CORE, Issue 6, May 2011.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

### Test Equipment Used

Table 11-2: First-Level Lightning Surge Tests (Telecommunications Type 1, 3, and 5 Ports) Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Overview (4.1)

Criteria:

R4-1 [231]      The equipment manufacturer shall classify all equipment ports associated with the EUT and the test laboratory shall clearly identify the classification of all ports in the Test Report for equipment that has been evaluated in accordance with Appendix B.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-1 [231].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Current-Limiting Protectors (4.2.2)

### Criteria:

R4-2 [232]      Equipment shall conform to Section 4, “Lightning and Power Fault,” without reliance on external secondary voltage or current-limiting protectors.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-2 [232].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Test Equipment (4.5.1)

Criteria:

R4-3 [26]    A declaration of the generator’s compliance shall be provided in the test report.

Oscilloscope plots of the waveforms for each lightning generator utilized, and a description of measurement results shall be part of the data sheet package or test

report for each product. Characterization of power fault generator waveforms is not

required.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-3 [26].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Interfacing With Agreed or Non-Field Replaceable Integrated Primary Protectors (4.5.9)

Criteria:

R4-4 [179]      If the equipment requires the use of an agreed/special primary protector, the manufacturer shall consult with the service provider to define and specify the agreed-upon primary protection.

R4-5 [181]      The manufacturer’s equipment documentation  shall state that the network equipment is not intended for deployment in CO-type facilities and shall specify the voltage-limiting and current-limiting characteristics of the agreed primary protection or the fixed integrated primary protection. Such characteristics are the maximum dc breakdown voltage and the voltage limiting of the surge protectors at different rates of rise (i.e., ±0.1 V/µs, ±100 V/µs, ±l000 V/µs).

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-4 [179] and R4-5 [181].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Short Circuit Test (Telecommunications Type 1, 3, and 5 Ports) (4.6.1.1)

Criteria:

R4-6 [25]        The EUT shall comply to the first- and second-level criteria of Section 4.5.7, “Conformance Criteria,” as a result of the application of a short-circuit (not greater than 1 Ω). The test shall be applied to all possible combinations of wiring conductors of the tested port for 30 minutes. For EUTs with more than one port of a given type, the conductors of all the ports of that type shall also be shorted together simultaneously.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-6 [25].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Ethernet Interface Considerations (Telecommunications Type 1, 2, 3, 3a/5a, 3b/5b, 4, 4A, or 5 ports. (4.6.1.2)

Criteria:

R4-7 [233]      All equipment Ethernet ports shall have adequate resistance to voltage surges. Ethernet ports shall be tested for resistance to lightning surges and power faults as specified in this document. Type 2 Ethernet ports per Appendix B meeting the exemption criteria of Section 4.6.2.1.4 are not required to withstand metallic surges. Refer to Conditions and Exemptions, page 4-41.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-7 [233].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Cell Site Inter-Structure Withstand Criteria (Telecommunications Type 3a/5a and 8b ports. (4.6.1.3)

Criteria:

R4-8 [234]      Type 3a/5a and Type 8b interfaces deployed between separate structures, cabinets, buildings, H-frames, and similar enclosures within a cell site shall demonstrate resistance to GPR via isolation or surge testing.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-8 [234].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Option B – Surge Test (4.6.1.3.2)

Criteria:

CR4-9 [235]    If required by a service provider, shielded Type 3a/5a and Type 8b ports shall demonstrate resistance to GPR via isolation or surge testing as if they are neither shielded nor in metallic conduit, notwithstanding the manufacturer’s installation requirements.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement CR4-9 [235].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## First-Level Lightning Criteria for Telecommunications Ports (Type 1, 3, 3b/5b, and 5 ports) (4.6.2.1.1)

Criteria:

R4-10 [27]      Telecommunications pairs that are exposed to OSP lightning surges (Type 1, 3, 3b/5b, and 5 ports) shall comply with first-level criterion of Section 4.5.7, “Conformance Criteria,” when subject to the applicable surge tests in Table 4-2.

R4-11 [167]    If the equipment port under test in R4-10 [27] contains a secondary protector with a voltage- limiting device, the applicable secondary protector test in Table 4-2 shall be performed at a reduced open-circuit voltage (Vs). Vs shall be the maximum operating peak threshold value of the voltage-limiting device(s) as described in Section 4.5.8.1, “Lightning — Secondary Protection.”

R4-12 [236]   The circuit packs of equipment exempt from Surge Test Number 4 of  Table 4-2 and Surge Test Number 1 of Table 4-3 shall be explicitly labeled to indicate that they must be installed in dedicated enclosures meeting the above specifications. Labeling is not required for circuit packs associated only with specific systems meeting the above criteria.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-10 [27], R4-11 [167], and R4-12 [236].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Test Procedure and Criteria for Surge Test Number 7 of Table 4-2 – high lightning exposure test for remote osp interfaces. (4.6.2.1.2.7)

Criteria:

CO4-13 [178]  Type 3 and Type 5 ports serving high-exposure, residential type facilities should maintain operation per the first-level criterion of Section 4.5.7 “Conformance Criteria,” when subjected to Surge Test Number 7 of Table 4-2, based on the Test Procedure Guidelines for this test. This test only applies if the equipment is intended for rural residential customer facilities predominantly fed by cable with less than 25 pairs, and where the maximum operating loop distance of the port is less than 1kft. In addition, this test should only be required at the request of the service provider based on the intent to deploy the EUT as described above and having a very high exposure risk to large surge events.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements CO4-13 [178].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Intra-Building or Intra-Site Lightning Criteria (Telecommunications Type 2, 3a/5a, 4, 4a ports. (4.6.2.1.3)

Criteria:

R4-14 [30]      Ports that remain intra-building or intra-site (Type 2, 3a/5a, 4, and 4a ports) and do not require shielded cables shall comply with first-level criteria of Section 4.5.7, “Conformance Criteria,” when subjected to the applicable surge tests in Table 4-2.

R4-15 [169]    If the equipment port under test in R4-14 [30] contains a secondary protector with a voltage-limiting device, the applicable secondary protector test in Table 4-2 shall be performed at a reduced open-circuit voltage (Vs). Vs shall be the maximum operating peak threshold value of the voltage-limiting device(s) as described in Section 4.5.8.1, “Lightning — Secondary Protection.”

R4-16 [31]      Equipment or subassembly ports that are intended to meet the criteria for Type 2, 3a/5a, 4, or 4a of this section, but do not meet, or are not intended to meet, the criteria for Type 1, 3, or 5 ports, shall contain the warning below or substantially similar warning in the equipment installation documentation.

R4-17 [170]    Ports that remain intra-building or intra-site (Type 2, 3a/5a, 4, and 4a ports) that require shielded cables shall comply with the first-level criteria of Section 4.5.7, “Conformance Criteria,” when subjected to Surge Test Number 16 (paired conductors) or Surge Test Number 17 (coaxial) of Table 4-2.

R4-18 [237]    If Type 2, 3a/5a, 4, or 4a ports of the equipment requires a shielded cable, the documentation shall contain a warning statement indicating that the intra-building port(s) of the equipment, or subassembly, is suitable for connection only to “shielded intra-building cabling that is grounded at both ends.” This requirement applies to paired conductor interfaces as well as coaxial interfaces (i.e., DS3). An example is shown below.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-14 [30], R4-15 [169], R4-16 [31], R4-17 [170] and R4-18 [237].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## First-Level Lightning Criteria for Antenna Ports (Telecommunications Type 6 Ports) (4.6.2.1.5)

Criteria:

R4-19 [209]    Type 6 ports shall comply with Surge Test Number 19 in Table 4-2. In addition, the manufacturer shall indicate in the equipment documentation  that external lightning protection shall be used that does not permit transients of a greater magnitude or duration than the transient specified in Surge Test Number 19 of Table 4-2.

R4-20 [238]    If the equipment port(s) under test in R4-19 [209] contain a secondary protector with a voltage-limiting device(s), Surge Test Number 19.1 in Table 4-2, shall be performed at a reduced open-circuit voltage (Vs). The voltage (Vs) shall be the maximum operating peak threshold value of the voltage-limiting device(s) as described in Section 4.5.8.1, “Lightning — Secondary Protection.”

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-19 [209] and R4-18 [238].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## First-Level Lightning Criteria for AC Power Ports (Telecommunications Type 7 Ports) (4.6.2.1.6)

Criteria:

R4-21 [210]    The manufacturer shall specify in the documentation whether an external Surge Protective Device (SPD) is intended to be used with the ac-powered equipment. The SPD, if used, is installed at the ac power service entrance (see definition in the NEC[62]).

R4-22 [32]      Type 7 ports that require external SPD protection to be present or installed shall comply with Surge Test Number 20 in Table 4-2. These criteria also apply to equipment connected to receptacles inside buildings such as computers, terminal adapters, rectifiers, etc.

R4-23 [211]    Type 7 ports that do not require external SPD protection to be present or installed shall comply with Surge Test Number 21 in Table 4-2 for this test and port type. This criterion also applies to equipment that is located in close proximity to the ac power service entrance (i.e., inside GR-487-CORE,[42] GR-950-CORE,[43] and GR-13-CORE[47] enclosures or that is pole mounted), or connected to major commercial ac feeders. This criterion generally is not required for equipment

connected to receptacles inside buildings such as computers, terminal adapters, rectifiers, etc.; however, if equipment does comply with this Requirement, it is considered compliant with R4-22 [32].

R4-24 [239]    If the equipment port(s) under test in R4-22 [32] or R4-23 [211] as applicable contain a secondary protector with a voltage-limiting device(s), Surge Test Number 21.1 in Table 4-2, as applicable, shall be performed at a reduced  open-circuit voltage (Vs). The voltage (Vs) shall be the maximum operating peak threshold value of the voltage-limiting device(s) as described in Section 4.5.8.1, “Lightning — Secondary Protection.”

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-21 [210], R4-22 [32], R4-23 [211], and R4-24 [239].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## DC Power to Antenna Lightning Criteria (Type 8a Ports) (4.6.2.1.7)

Criteria:

R4-25 [240]    DC power ports that serve equipment at the top of antennas to provide or receive power (Type 8a ports) shall comply with the first-level criterion of Section 4.5.7, “Conformance Criteria,” when subjected to Surge Test Number 22 of Table 4-2.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-25 [240].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Second-Level Lightning for Telecommunication Ports (Type 1, 3, and 5 Ports) (4.6.3.1)

Criteria:

R4-26 [29]      As a result of the application of Surge Test Number 1 in Table 4-3 based on the Test Procedure Guidelines for this test and port type, the EUT (e.g., the surged telecommunications ports) including the host system shall not become a fire, fragmentation, or safety-related hazard as described in the second-level conformance criterion in Section 4.5.7, “Conformance Criteria.”

R4-27 [241]    The circuit packs of equipment exempt from Surge Test Number 4 of

Table 4-2 and Surge Test Number 1 of Table 4-3 shall be explicitly labeled to indicate that they must be installed in dedicated enclosures meeting the above specifications. Labeling is not required for circuit packs associated only with specific systems meeting the above criteria.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-26 [29] and R4-27 [241].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Second-Level Lightning for AC Power Ports (Type 7 Ports) (4.6.3.2)

Criteria:

R4-28 [33]      This requirement applies to all Type 7 ports. As a result of the application of Surge Test Number 2 in Table 4-3, the EUT including the host system shall not become a fire, fragmentation, or safety-related hazard as described in the second- level conformance criteria in Section 4.5.7, “Conformance Criteria.” These criteria typically apply to equipment connected to receptacles inside buildings such as computers, terminal adapters, rectifiers, etc.

R4-29 [242]    If the equipment port(s) under test in R4-28 [33] contain a secondary protector with a voltage-limiting device(s), Surge Test Number 2.1 in Table 4-3, as applicable, shall be performed at a reduced open-circuit voltage (Vs). The reduced open-circuit voltage (Vs) shall be the maximum operating peak threshold value of the voltage-limiting device(s) as described in Section 4.5.8.1, “Lightning — Secondary Protection.”

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-28 [33] and R4-29 [242].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## First-Level Power Fault/Induction Requirements (4.6.4.1)

Criteria:

R4-30 [35]      After the application of the specified tests in Table 4-4, the EUT including the host system shall not be damaged and shall continue to operate properly as described in Section 4.5.7.1, “First-Level Criteria.”

R4-31 [172]    If the equipment port under test in R4-30 [35] contains a secondary protector with a voltage-limiting device, Tests 1.1, 2.1, and 3.2 in Table 4-4 shall be performed. The test voltage Vs shall be determined from the maximum operating peak threshold value of the voltage-limiting device. The maximum operating peak threshold value of the voltage-limiting device is described in Section 4.5.8.2, “Power Fault — Secondary Protection.” The Vs rms value applied is 0.707 × the maximum operating peak threshold value. If Vs (.707) exceeds the voltage for Surge Test Numbers 1, 2, or 3.1 or is less than 25 Vrms, the reduced voltage test does not need to be performed. The host system shall not be damaged and shall continue to operate properly as described in Section 4.5.7.1, “First-Level Criteria.”

R4-32 [173]    If the equipment port under test contains a secondary protector with a self- resettable current-limiting device (e.g., PTC) that operated during Tests 1, 2, or

3.1 in Table 4-4, Tests 1.2, 2.2, and 3.3 shall be performed at a reduced rms current level at the maximum operating threshold value of the current-limiting device. The

maximum operating threshold value of the current-limiting device is described in

Section 4.5.8.2, “Power Fault — Secondary Protection.” The host system shall not be damaged and shall continue to operate properly as described in Section 4.5.7.1,

“First-Level Criteria.”

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-30 [35], R4-31 [172] and R4-32 [173].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Second-Level Power Fault Requirements (4.6.4.2)

Criteria:

R4-33 [40]      This Requirement applies only to Type 3a/5a, 3b/5b, 4, and 4a ports of network equipment intended to be located within (or on) customer buildings that will neither interface with the telecommunications  OSP nor serve off-premises equipment (see Appendix B). An example might be an ONT or PBX located at the customer facility with POTS or Ethernet ports only connected to telephones or Ethernet equipment located within that facility. The test is to be applied to equipment ports that interface with paired telecommunications conductors. As a result of the application of Surge Test Number 1 in Table 4-5, the EUT including the host system shall not become a fire or fragmentation hazard as described in the second-level conformance criteria in Section 4.5.7, “Conformance Criteria.” These criteria apply to equipment ports even if the telecommunication cable is shielded and both ends of the shield are grounded.

R4-34 [41]      Equipment or a subassembly that meets the requirements of R4-33 [40], but does not meet, or is not intended to meet, the criteria of all the applicable tests of Table 4-5, shall contain the following, or substantially similar, warning in the equipment installation documentation:

WARNING:  The intra-building ports of the equipment or subassembly is suitable for connection to intra-building or unexposed wiring or cabling only. The intra-building port(s) of the equipment or subassembly MUST NOT be metallically connected to interfaces that connect to the OSP or its wiring. These interfaces are designed for use as intra-building interfaces only (Type 2 or Type 4 ports as described in GR-1089-CORE) and require isolation from the exposed OSP cabling. The addition of Primary Protectors is not sufficient protection in order to connect these interfaces metallically to OSP wiring.

R4-35 [36]      This requirement applies to Type 1, Type 3, and Type 5 ports. As a result of the application of second-level power fault tests shown in Table 4-5, the EUT (e.g., the surged telecommunications ports) including the host system shall not become a fire, fragmentation, or safety-related hazard as described in the second-level conformance criterion in Section 4.5.7, “Conformance Criteria.”

R4-36 [174]    If the equipment port under test in R4-35 [36] contains a secondary protector with voltage-limiting device, the undervoltage test (Surge Test Numbers 2.1, 3.1 and

4.1 or 4.2) in Table 4-5 shall be performed at Vs, (the open-circuit voltage at the maximum operating peak threshold value of the voltage-limiting device). The

maximum operating peak threshold value of the voltage-limiting device is described in Section 4.5.8.2, “Power Fault — Secondary Protection.” The rms value applied is 0.707 × the maximum operating peak threshold value. If the reduced value for this requirement is greater than the values in Table 4-5 for the applicable Surge Test Numbers 2, 3, 4, or less than 25 Vrms, the reduced voltage test need not be performed. As a result of the application of the surges, the EUT (e.g., the surged telecommunications ports) including the host system shall not become a fire, fragmentation, or safety-related hazard as described in the second-level conformance criteria in Section 4.5.7, “Conformance Criteria.”

R4-37 [175]    If the equipment port under test in R4-35 [36] contains a current-limiting device, Surge Test Number 4.3 in Table 4-5 shall be performed at a reduced rms current level at the maximum operating threshold value of the current-limiting device(s) (Is Table 4-5) or 2.2A, whichever is lower. The maximum operating threshold value of the current-limiting device(s) is described in Section 4.5.8.2,“Power Fault — Secondary Protection.” As a result of the application of the surges, the EUT (e.g., the surged telecommunications ports) including the host system shall not become a fire, fragmentation, or safety-related hazard as described in the second-level conformance criteria in Section 4.5.7, “Conformance Criteria.”

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-33 [40], R4-34 [41], R4-35 [36], R4-36 [174] and R4-37 [175].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Criteria for Equipment With Integrated Primary Protection (4.7)

Criteria:

R4-38 [182]    EIPP composed solely of components that comply with Telcordia Generic Requirements applicable to each component is considered compliant with most of the requirements in this section. Such equipment shall still comply with Section 4.7.1, “Equipment Classification,” Section 4.7.2, “Protector Requirements,” and Section 4.7.5, “Dielectric Withstand.”

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-38 [182].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Classification (4.7.1)

Criteria:

R4-39 [183]    EIPP installation documentation shall contain the following, or substantially similar, warning:

WARNING:  This equipment contains integrated primary protection. This equipment is not suitable for installation in CO and network locations such as CEVs and huts that contain other primary protection for OSP cable. The equipment may be located in Electronic Equipment Cabinets (EECs) where appropriate installation practices are used. For example, installation should not employ a separate primary protector for the equipment; appropriate cabling should be run to the equipment, etc.

WARNING:  For the purposes of determining placement and location of fuse links or fuse cable, the equipment shall be treated as a fuse-less protector, regardless of any capability to provide fusing.

R4-40 [184]    The manufacturer shall classify EIPP as being acceptable for one or more of the following conditions:

1. Installation at OSP locations and having or containing components or circuitry that act as OSP fuse links inside the EUT.

2. Installation at OSP locations and not having or containing components or circuitry that act as OSP fuse links inside the EUT.

3. Installation in subscriber locations (i.e., business/residential buildings or structures) and having or containing components or circuitry that act as OSP fuse links inside the EUT.

4. Installation in subscriber locations (i.e., business/residential buildings or structures) and not having or containing components or circuitry that act as OSP fuse links inside the EUT.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-39 [183] and R4-40 [184].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Protector Requirements (4.7.2)

Criteria:

R4-41 [185]    Any primary protector units installed or shipped with the EIPP shall be Listed.

Embedded or non-field replaceable primary protector components shall be Listed or

Recognized.

NOTE: Examples of appropriate Listing standards for primary protection are

UL 497[50] and UL 497C.[53]

R4-42 [186]    EIPP shall be Listed. The Listing program shall address requirements related to primary protection.

R4-43 [187]    EIPP classified as suitable for installation at the subscriber location under items 3 or 4 in R4-40 [184], shall:

• Contain or have provisions for installation of a Listed primary protector, or

• Be Listed as a primary protector, or

• Have non-field replaceable primary protection devices that comply with

GR-3154-CORE,[34] GR-974-CORE,[33] or GR-1361-CORE.[40]

As an exception to this, EIPP that is a part of a Network-powered Broadband Communication System covered by NEC[62] Article 830 may contain embedded protection provided the EIPP is Listed for this application.

R4-44 [188]    EIPP shall be marked or labelled externally to indicate that it contains primary protection.

R4-45 [189]    The primary protector assembly or discrete protector, such as a gas tube, supplied with the equipment shall be appropriate for the application based on relevant performance specifications. Appropriateness may be demonstrated by data supplied by the protector manufacturer or testing.

NOTE: Examples of specifications for primary protector assemblies are in the Telcordia documents GR-3154-CORE,[34] GR-974-CORE,[33] and

GR-1361-CORE.[40] If the EUT contains an embedded primary protector

other than a 5-pin protector, a subset of requirements of GR-974-CORE (or GR-1361-CORE) may be applicable to that type of protector assembly.

Manufacturers are expected to consult with the service provider to ensure the protector(s) is appropriate for the application.

R4-46 [190]    The manufacturer shall describe in the equipment documentation the protector characteristics, such as voltage limiting, needed to determine that the primary protection is appropriate for the electrical environment. Such characteristics are the maximum dc breakdown voltage and the voltage limiting of the surge protectors at different rates of rise (i.e., ±0.1 V/µs, ±100 V/µs, ±l000 V/µs).

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-41 [185], R4-42 [186], R4-43 [187], R4-44 [188], R4-45 [189] and R4-46 [190].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Lightning Surge and Power Fault Tests for Protected Circuits (4.7.3)

Criteria:

R4-47 [191]    The EIPP port under test shall comply with all of the applicable first- and second-level criteria for equipment interfacing with the OSP in Section 4. Current- limiting elements of agreed-upon primary protection or non-field replaceable primary protection are allowed to remain in the circuit during this testing.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-47 [191].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Fusing Coordination for Circuits That Contain Components or Circuitry That Act as osp fuse links (4.7.4.1)

Criteria:

R4-48 [193]    The unprotected circuit shall not become a fire, fragmentation, or electrical safety hazard, as described in the second-level conformance criterion in Section 4.5.7, “Conformance Criteria,” as a result of conducting the currents specified in Table 4-7 at the specified durations. The unprotected circuit, including the cable stub, is permitted to open the circuit and interrupt the current during the test.

The fusing duration corresponding to 24-AWG stub cable shall be used for EUT that does not have a stub cable. If the EUT has a stub cable, then the duration corresponding to 24- or 26-AWG stub cable shall be chosen depending on the size of conductors in the stub cable. The duration corresponding to 24-AWG stub cable shall be used for EUT that has a stub cable coarser than 24 AWG. The open-circuit voltage for each test shall be at least 425 Vrms. The fire hazard indicator described in Section 4.5.7.2 is to be used for the EUT and the stub cable.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-48 [193].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Enclosure Suitable for Fusing (4.7.4.1.1)

Criteria:

R4-49 [194]    If the EIPP enclosure is made of metal, the minimal thickness of the enclosure, including doors and covers, shall not be less than 0.0356 inch, including manufacturing tolerances (e.g., 20-gauge).

R4-50 [195]    EIPP enclosures may be made of polymeric materials. If made of polymeric materials, the minimal thickness of the enclosure, including doors and covers, shall not be less than 0.125 inch. Parts of the enclosure within 4 inches of integrated primary protectors or conductive parts of the unprotected circuit shall be constructed of polymeric material rated CSA 0.17-5VA or UL 94-5VA.

R4-51 [196]    The enclosure shall not contain vents or openings that would allow ejection of molten metal or flames or similar hazards if internal fusing occurs.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-49 [194], R4-50 [195] and R4-51 [196].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Fusing Coordination for Circuits Not Containing Components or Circuitry That Act as osp fuse links (4.7.4.2)

Criteria:

R4-52 [199]    The unprotected circuit shall be capable of conducting the currents specified in Table 4-7, “Fusing Coordination for Unprotected Circuits,” for the specified durations without becoming a fire, fragmentation, or electrical safety hazard. In addition, at the conclusion of Tests 1, 2, and 3, the circuits upstream of the voltage- limiting element of the primary protection shall not be damaged or degraded. At the conclusion of all tests, a short circuit shall remain between each input terminal of the EUT and ground.

The fusing duration corresponding to 24-AWG stub cable shall be used for EUT that does not have a stub cable. If the EUT has a stub cable, then duration corresponding to 24- or 26-AWG stub cable shall be chosen depending on the size of conductors in the stub cable. The duration corresponding to 24-AWG stub cable shall be used for EUT that has a stub cable coarser than 24 AWG.

The 26-AWG or coarser conductors of the stub cable are permitted to fuse open during the test. This fusing shall be permitted within the stub cable. Fusing of the stub cable conductors within the EUT enclosure shall not be permitted. If fusing occurs within the stub cable, the stub cable shall meet Requirements R4-54 [201] and R4-55 [202].

The open-circuit voltage for each test shall be sufficient to generate the required current. One circuit shall be used for each test condition except for Tests 1 and 2, which require 6 conductors. The fire hazard indicator described in Section 4.5.7.2 is to be used for the EUT and the stub cable. The test source is to be connected to the EUT with 22-AWG or coarser conductors if an EUT stub cable is not provided.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-52 [199]

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Dielectric Withstand (4.7.5)

Criteria:

R4-53 [200]    The unprotected circuit shall be capable of withstanding a test voltage of 1500 Vdc or 1000 Vrms applied between each electrically isolated circuit and all other electrically isolated circuits and grounded metal parts. Tip and Ring conductors of each unique electrically isolated circuit shall be shorted together. All capacitors to grounded metal parts can be disconnected before testing if it is desired. All semiconductors including voltage-limiting devices and discharge resistors that provide a path to ground shall be disconnected before testing.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-53 [200]

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## EIPP Cable Requirements (4.7.6)

Criteria:

R4-54 [201]    The EIPP protector cable shall be appropriate for the application based on relevant performance specifications. Appropriateness may be demonstrated by data supplied by the cable manufacturer or testing.

NOTE: For an example of cable specifications, see GR-421-CORE.[36] Manufacturers are expected to consult with the service provider to ensure the protector(s) is appropriate for the application.

R4-55 [202]    The EIPP protector cable shall have all conductors under a grounded metal shield or metal EUT enclosure. The plastic core wrap and any corrugated metallic shield, as well as the PVC sheath, shall terminate inside the EIPP enclosure. The conductors shall be terminated inside the EIPP to the primary protectors or protector mounting mechanism. Bushings shall meet the 5-inch flame test of UL 746C.[55]

The EIPP protector cable shall be fastened to the EUT enclosure in a manner that provides a positive ground and is able to withstand a pulling force equal to 30 pounds of pull for 1 minute when applied in the downward direction at 2 feet from the cable entrance in all directions.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirements R4-54 [201] and R4-55 [202].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## AC Power Fault Immunity — Unprotected Circuits (4.7.7)

Criteria:

R4-56 [203]    The unprotected circuits shall not be damaged and shall continue to operate properly after the application of the 60-Hz currents of Table 4-8. One unprotected circuit shall be analyzed for each condition.

NOTE: This test is not required if compliance with these requirements was demonstrated during Surge Tests 6–8 of Table 4-5.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-56 [203].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Lightning Surge Tests — Unprotected Circuits (4.7.8)

Criteria:

R4-57 [204]    The EUT shall not become a fire, fragmentation, or safety-related hazard after application of second-level surge tests in Table 4-9. The fire hazard indicator described in Section 4.5.7.2 is to be used for the EUT and the stub cable. If the EUT has more than 10 protector positions, a total of 10 protector positions shall be tested. If the EUT has less than 10 protector positions, all positions shall be tested.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Requirement R4-57 [204].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Lightning Surge Tests for Severe Climatic Conditions — Unprotected Units (4.7.8.1)

Criteria:

CR4-58 [205]  The EUT shall not be damaged and shall be capable of operating properly after application of first-level surge tests in Table 4-10 when tested as outlined in Section 4.7.8, excluding the test from Table 4-9. All protector positions shall be tested up to a maximum of 10.

CR4-59 [206]  The EUT shall not become a fire, fragmentation, or safety-related hazard after application of second-level surge tests in Table 4-10 when tested as outlined in Section 4.7.8, excluding the test from Table 4-9. The fire hazard indicator described in Section 4.5.7.2 is to be used for the EUT and the stub cable. All protector positions shall be tested up to a maximum of 10.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results:

The <Product Name> was compliant/ not compliant with Critical Requirements CR4-58 [205] and CR4-59 [206].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

<<Insert tables with detailed description of equipment pack fill>>