TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

Part 14

ELECTRICAL SAFETY

Section 7, GR-1089-CORE

Telcordia Technologies GR-1089, Issue 6, May 2011

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Page

Test Results Summary	4

Overview	6

Listing Requirements (7.2)	7

Classification of Voltages (7.3)	8

Continuous Voltage and Current Limits (7.3.1)	10

Class A1 Voltage Accessibility Requirements (7.4.1)	11

Class A2 Voltage Accessibility Requirements (7.4.2)	13

Class A3 Voltage Accessibility Requirements (7.4.3)	14

Class AB Voltage Accessibility Requirements (7.4.4)	16

Class B Voltage Accessibility Requirements (7.4.5)	18

Interrupted/Tripped Sources (7.5.1)	20

Transient Sources (7.5.3)	22

Power Limitation Requirement (7.6)	23

Leakage Current Requirements for Large Area Contact (7.7.2.1)	24

Leakage Current Requirements for Small Area Contact (7.7.2.2)	25

Leakage Current Between Surfaces of Equipment (7.7.2.3)	26

Appendix A	27

- LIST OF TABLES

Page

Table 14-1 Electrical Safety Summary of Test Results	4

Table 14-2: Equipment Sources and Classifications	8

Table 14-3: Classification of Voltages List of Test Equipment	9

Table 14-4: Continuous Voltage and Current Limits Detailed List of Test Equipment	10

Table 14-5: Class A1 Voltage Sources and Accessibility	11

Table 14-6: Class A1 Voltage Accessibility Detailed List of Test Equipment	12

Table 14-7: Class A2 Voltage Sources and Accessibility	13

Table 14-8: Class A2 Voltage Accessibility Detailed List of Test Equipment	13

Table 14-9: Class A3 Voltage Sources and Accessibility	14

Table 14-10: Class A3 Voltage Accessibility Detailed List of Test Equipment	15

Table 14-11: Class AB Voltage Sources and Accessibility	16

Table 14-12: Class AB Sources Detailed List of Test Equipment	17

Table 14-13: Class B Voltage Sources and Accessibility	18

Table 14-14: Class B Sources Detailed List of Test Equipment	19

Table 14-15: Interrupted/ Tripped Sources Detailed List of Test Equipment	21

Table 14-16: Transient Sources Detailed List of Test Equipment	22

Table 14-17: Power Limitation Detailed List of Test Equipment	24

Table 14-18: Leakage Current for Large Area Contact Detailed List of Test Equipment	25

Table 14-19: Leakage Current for Small Area Contact Detailed List of Test Equipment	26

Table 14-20: Leakage Current Between Surfaces Detailed List of Test Equipment	27

- LIST OF FIGURES

Page

Error! No table of figures entries found.

## Test Results Summary

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-1089-CORE.

- Section Name column gives the Section name from GR-1089-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-1089-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, non-compliant, etc.).

- Compliant: The Equipment Under Test (<Product Name>) met the requirements of the corresponding criteria.

- Non-compliant: The <Product Name> did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to the <Product Name>.

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- For additional details go to the page listed in the Page column.

- Page column gives the page number, of this report, for the corresponding criteria.

Table 14-1 Electrical Safety Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Comments | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 7. | Electrical Safety Criteria | - | - |  | - |
| 7.2 | Listing Requirements | R7-1 [22] |  |  | 7 |
|  |  | R7-2 [23] |  |  | 7 |
|  |  | R7-3 [24] |  |  | 7 |
| 7.3 | Classification of Voltages | R7-4 [143] | - |  | 8 |
| 7.3.1 | Continuous Voltage and Current Limits | R7-5 [115] |  |  | 10 |
|  |  | R7-6 [144] |  |  | 10 |
| 7.4 | Continuous Source Requirements | - | - |  | - |
| 7.4.1 | Class A1 Voltage Accessibility Requirements | R7-7 [54] |  |  | 11 |
| 7.4.2 | Class A2 Voltage Accessibility Requirements | R7-8 [55] |  |  | 13 |
| 7.4.3 | Class A3 Voltage Accessibility Requirements | R7-9 [56] |  |  | 14 |
|  |  | R7-10 [57] |  |  | 14 |
|  |  | R7-11 [58] |  |  | 14 |
| 7.4.4 | Class AB Voltage Accessibility Requirements | R7-12 [59] |  |  | 16 |
|  |  | R7-13 [60] |  |  | 16 |
|  |  | R7-14 [61] |  |  | 16 |
|  |  | R7-15 [62] |  |  | 16 |
| 7.4.5 | Class B Voltage Accessibility Requirements | R7-16 [63] |  |  | 18 |
| 7.5 | Duration-Limited Source Requirements | - | - |  | - |
| 7.5.1 | Interrupted/Tripped Sources | R7-17 [64] |  |  | 20 |
|  |  | R7-18 [65] |  |  | 20 |
|  |  | R7-19 [66] |  |  | 20 |
|  |  | R7-20 [145] |  |  | 20 |
| 7.5.2 | Transient Sources | R7-21 [67] |  |  | 22 |
| 7.6 | Power Limitation Requirement | R7-22 [68] |  |  | 23 |
| 7.7 | Leakage Currents from Exposed Surfaces | - | - |  | - |
| 7.7.2.1 | Leakage Current Requirements for Large Area Contact | R7-23 [69] |  |  | 25 |
| 7.7.2.2 | Leakage Current Requirements for Small Area Contact | R7-24 [70] |  |  | 26 |
| 7.7.2.3 | Leakage Current Between Surfaces of Equipment | R7-25 [71] |  |  | 27 |
| 7.8 | Laser Safety and Labeling Criteria | R7-26 [246] |  |  | 28 |

NA: Not Applicable

## Overview

### Project Objective

Testing was performed to determine if the <Product Name> met the requirements for Section 7, Electrical Safety Criteria, of Telcordia Technologies GR-1089-CORE, Issue 6, May 2011.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

## Listing Requirements (7.2)

### Criteria:

R7-1 [22]	All network equipment that is directly powered by commercial ac, either through a hard-wire or plug-and-cord connection, shall be Listed.

R7-2 [23]	Inverters that provide power to network equipment or to convenience receptacles shall be Listed.

R7-3 [24]	Network communications equipment that is intended to be located on customer premises shall be Listed.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-1[22], Requirement R7-2 [23] and Requirement R7-3 [24].

## Classification of Voltages (7.3)

### Criteria:

R7-4 [143]	Electrical safety testing shall be performed with EUT energized as in normal operation. Where applicable, external voltage sources, i.e., voltages applied to EUT by other equipment, shall be present during testing. In the case that the external source cannot be specifically identified, the source shall be classified considering the worst case of GR-1089-CORE class source that is expected to connect to the EUT.

When EUT generates voltages, the electrical safety testing shall be performed including the host system. The sources appearing on the EUT and the sources on the host system arising from the EUT shall be classified.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-4 [143].

Table 14-2: Equipment Sources and Classifications

<List ALL sources and their classification.>

| Source | Classification |
| --- | --- |

### Test Equipment Used

Table 14-3: Classification of Voltages List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Continuous Voltage and Current Limits (7.3.1)

### Criteria:

R7-5 [115]	Continuous source voltage limits (and current limits, as appropriate) shall apply between each terminal and ground with all other terminals connected as in normal service. The limits shall also apply between each terminal and ground with all other terminals open circuited. For paired-conductor sources, i.e., telecommunications or similar circuits, the limits also shall apply with all other terminals individually grounded.

R7-6 [144]	Sources utilizing ground fault detection or voltage shutdown shall be evaluated against transient sources requirements of Section 7.5.2.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-5 [115] and Requirement R7-6 [144].

### Test Equipment Used

Table 14-4: Continuous Voltage and Current Limits Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Class A1 Voltage Accessibility Requirements (7.4.1)

### Criteria:

R7-7 [54]	Class A1 voltage sources shall be inaccessible or have restricted access for contact by the general public and may be exposed for contact by employees and craftspersons. Shrouded or guarded connections or sources with Class A1 voltages appearing on their pins or “connection means” (i.e., screws, headers, wire wrap posts, gold fingers, etc.) are considered to provide adequate protection of the general public and employees from these sources.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-7 [54].

Table 14-5: Class A1 Voltage Sources and Accessibility

<List A1 sources and their limit of accessibility>

| Source | Classification | Accessibility |
| --- | --- | --- |

### Test Equipment Used

Table 14-6: Class A1 Voltage Accessibility Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Class A2 Voltage Accessibility Requirements (7.4.2)

### Criteria:

R7-8 [55] 	Class A2 voltage sources shall be inaccessible for contact by the general public, shall be inaccessible or have restricted access for contact by employees, and may be exposed for contact by craftspersons. The general public and employees are adequately protected from contact with Class A2 voltages if these sources appear on the pins or other “connection means” of shrouded or guarded connectors or sources.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-8 [55].

Table 14-7: Class A2 Voltage Sources and Accessibility

<List A2 sources and their limit of accessibility>

| Source | Classification | Accessibility |
| --- | --- | --- |

### Test Equipment Used

Table 14-8: Class A2 Voltage Accessibility Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Class A3 Voltage Accessibility Requirements (7.4.3)

### Criteria:

R7-9 [56]	Class A3 voltage sources shall be inaccessible for contact by the general public and employees. Equipment that is powered by or that generates Class A3 voltage shall have restricted access for contact by craftspersons or shall be exposed for contact by craftspersons with the following precautions.

R7-10 [57]	When an enclosure or baffle is removed, or energized electrical circuits are otherwise exposed for contact by craftspersons, Class A3 sources shall be segregated from Class A1 and Class A2 sources by appropriate insulation, baffling, or location to prevent inadvertent contact.

R7-11 [58]	Designed appearances of Class A3 voltage sources on equipment that is powered by or that generates such voltages shall be labeled where craftspersons are normally intended to contact them for service operation.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R7-9 [56], R7-10 [57], and R7-11 [58].

<Explain how Class A3 sources were segregated from Class A1 and Class A2 sources.>

<State if a Class A3 warning label was present, or why it was not needed.>

Table 14-9: Class A3 Voltage Sources and Accessibility

<List A3 sources and their limit of accessibility.>

| Source | Classification | Accessibility |
| --- | --- | --- |

### Test Equipment Used

Table 14-10: Class A3 Voltage Accessibility Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Class AB Voltage Accessibility Requirements (7.4.4)

### Criteria:

R7-12 [59]	Class AB voltage sources shall be restricted to systems powering applications confined to the outside plant and utilizing COAX.

R7-13 [60]	Class AB voltage sources shall be inaccessible for contact by the general public and employees. Equipment that is powered by, or that generates, Class AB voltage shall have restricted access for contact to the Class AB voltage by craftspersons.

R7-14 [61]	Bare-handed contact with Class AB voltages shall not be permitted. Rubber gloves and eye protection shall be worn when working on conductors energized to Class AB voltages.

R7-15 [62]	Designed appearances of Class AB voltage sources on equipment that is powered by, or that generates, such voltages shall be labeled where craftspersons are normally intended to access them for service operations.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R7-12 [59], R7-13 [60], R7-14 [61], and R7-15 [62].

Table 14-11: Class AB Voltage Sources and Accessibility

<List Class AB sources and their limit of accessibility.>

| Source | Classification | Accessibility |
| --- | --- | --- |

### Test Equipment Used

Table 14-12: Class AB Sources Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Class B Voltage Accessibility Requirements (7.4.5)

### Criteria:

R7-16 [63]	Class B voltage sources shall be de-energized before contact is allowed. With normal equipment enclosures in place, it shall not be possible to contact Class B sources with the test finger shown in Figure 7-4 where dimension “A” is 9 cm (3.54 inches). Protection covers carrying warning labels for Class B sources shall not be removable without the use of tools and/or a key. When an enclosure or baffle is removed to permit access to Class A1, A2, or A3 sources, Class B sources shall have restricted access for contact by craftspersons.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-16 [63].

Explain how Class B sources had restricted access for contact by craftsperson if an enclosure or baffle was removed to permit access to Class A1, A2, or A3 sources.

Table 14-13: Class B Voltage Sources and Accessibility

<List Class B sources.>

| Source | Classification | Accessibility |
| --- | --- | --- |

### Test Equipment Used

Table 14-14: Class B Sources Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Interrupted/Tripped Sources (7.5.1)

### Criteria:

R7-17 [64]	Interrupted/tripped voltages shall be less than 300 volts peak-to-peak and less than 200 volts peak-to-ground as measured across a resistive termination of at least one MΩ.

R7-18 [65]	The voltage shall be interrupted to create idle intervals of at least 1 second (continuous) duration, each separated by no more than 5 seconds. During the idle intervals, the voltage to ground shall not exceed Class A2 voltage limits.

R7-19 [66]	Interrupted/tripped voltage sources shall include a series current-sensitive tripping device in the current lead that will trip the voltage as shown in Figure 7-6 and/or, provide a voltage to ground (“monitoring” voltage) on the tip or ring conductor with a magnitude of at least 19 volts peak (but not to exceed the Class A2 limits) when the interrupted voltage is not present (idle interval). Tripping devices and/or “monitoring” voltages shall be incorporated in the equipment, depending on the current flow through specified resistances connected between the interrupted/ tripped source and ground as follows:

a. If the current through a 500-ohm and greater resistor does not exceed 100 mA peak-to-peak, neither a tripping device nor a “monitoring” voltage is required.

b. If the current through a 500-ohm and greater resistor exceeds 100 mA peakto-peak but does not exceed this value of current with a 1500-ohm and greater resistor, the interrupted/tripped source shall include either a tripping device that meets the operating characteristics shown in Figure 7-5 for a resistance of 500 ohms and greater, or a “monitoring” voltage.

c. If the current through a 1500-ohm and greater resistor exceeds 100 mA peakto-peak, the interrupted source shall include a tripping device. If the tripping device meets the operating characteristics shown in Figure 7-5 for a resistance of 500 ohms and greater, then no “monitoring” voltage is required. If the tripping device only meets the operating characteristics shown in Figure 7-5 for a resistor of 1500 ohms and greater, then the interrupted source shall also include a “monitoring” voltage.

R7-20 [145]	Substantiating data provided by an NRTL for testing interrupted/tripped voltages as part of a successfully completed listing program, is acceptable as an indication of compliance with the criteria of Section 7.5.1. An example of an acceptable listing standard is UL60950-1,[33] Method B as described in Annex M.3.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R7-17 [64], R7-18 [65], R7-19 [66] and R7-20 [145].

### Test Equipment Used

Table 14-15: Interrupted/ Tripped Sources Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Transient Sources (7.5.2)

### Criteria:

R7-21 [67]	The peak voltage of a transient source may exceed 200 volts peak, but shall not exceed its intended continuous or duration-limited classification limit for longer than 0.01 second. The transient source shall deliver no more than 2 joules into a 500-ohm resistive load during the 0.01s transient interval.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-21 [67].

### Test Equipment Used

Table 14-16: Transient Sources Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Power Limitation Requirement (7.6)

### Criteria:

R7-22 [68]	Sources that may be applied to communication wiring shall have a functional design rated output (power rating) not greater than 100VA and a current rating not greater than 100/Vmax, where Vmax is the maximum output voltage regardless of load with rated input applied. The output power rating is the maximum power that the source is designed to supply over the communications wiring to any intended load circuit under normal operating conditions, including power dissipated in the cabling. Paralleling of power sources over multiple communications wires for the purpose of delivering power in excess of 100VA to a single load circuit shall not be permitted. This power limitation is not intended to apply to the CO power and battery plant.

This power limitation is not intended to preclude the use of several individual 100 VA power sources, each of which feeds a separate set of communications lines to a separate remote load circuit.

The maximum continuous current from sources that may be applied to communication wiring under normal conditions shall be consistent with its power rating, but shall not exceed 1.3 A unless the ampacity of the network wiring and current rating of network connectors and other network components is specified at a higher value and controlled. The maximum output current (Imax) under overload and fault conditions shall not exceed 150/Vmax or 2.4 A, whichever is less.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-22 [68].

### Test Equipment Used

Table 14-17: Power Limitation Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Leakage Current Requirements for Large Area Contact (7.7.2.1)

### Criteria:

R7-23 [69]	The current from any 100 cm2 (15.50 in2.) area or the entire area, whichever is smaller, of exposed surface (excluding grounded metal surfaces) measured in a 1500-ohm resistor connected between the area and ground shall be less than 0.3 mA peak.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-23 [69].

### Test Equipment Used

Table 14-18: Leakage Current for Large Area Contact Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Leakage Current Requirements for Small Area Contact (7.7.2.2)

### Criteria:

R7-24 [70]	The current from any 1 cm2 (0.16 in2.) area of exposed surface (excluding grounded metal surfaces) measured in a 10,000-ohm resistor connected between the area and ground shall be less than 0.15 mA peak.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-24 [70].

### Test Equipment Used

Table 14-19: Leakage Current for Small Area Contact Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Leakage Current Between Surfaces of Equipment (7.7.2.3)

### Criteria:

R7-25 [71]	The current measured in a 10,000-ohm resistor connected between any two areas of exposed surface (excluding grounded metal surfaces) of 1 cm2 (0.16 in2.) each shall be less than 0.15 mA peak.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-25 [71].

### Test Equipment Used

Table 14-20: Leakage Current Between Surfaces Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Laser Safety and Labeling Criteria (7.8)

### Criteria:

R7-26 [246]	Equipment containing LASER sources of Class 2 or higher shall contain Warning, Explanatory and Aperture labels and documentation in accordance with 21 CFR 1040.10 or IEC 60825-2.

Note: Listed products are considered compliant with this requirement

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R7-26 [246].

### Test Equipment Used

Table 14-211: Laser Safety and Labeling Criteria Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

<<Insert tables with detailed description of equipment pack fill>>