TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

Part 16

bonding and grounding

Section 9, GR-1089-CORE

Telcordia Technologies GR-1089, Issue 6, May 2011

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Page

Summary of Test Results	4

Overview	7

General Requirements Principles (9.2)	8

Equipment Grounding Systems (9.3)	9

Common Bonding Network (CBN) (9.3.1)	10

AC Equipment Grounding (9.4)	11

Communication Equipment Grounding (9.5)	13

Network Telecommunication Facilities (9.5.1)	14

Locations Where the NEC Applies (9.5.2)	16

Outside Plant (9.5.3)	17

Equipment Unit Bonding and Grounding (9.6)	18

Provisions for Equipment Unit Assembly Bonding and Grounding (9.7)	19

Connectors and Connection Methods for Equipment Unit Assemblies (9.7.1)	21

Bonding of Circuit Packs (9.7.2)	23

Centralized Power Sources (9.8.1)	24

Embedded Power Sources (9.8.2)	25

Bonding of Battery Return (BR) Input Terminals (9.8.3)	27

Bonding and Grounding Conductors (9.9.1)	29

Connections (9.9.2)	30

Connectors (9.9.3)	32

DC Power Sources (9.10.1)	33

AC Power Sources (9.10.2)	36

Test Environment - Compatibility of Former IBN Equipment with CBN Currents (9.12.1.7)	38

Identification of Test Points - Compatibility of Former IBN Equipment with CBN Currents (9.12.2)	39

DC Fault Test (9.12.3)	40

Frame EFT Test (9.12.4)	41

Frame Surge Test (9.12.5)	42

AC Fault Test (9.12.6)	43

Grounding Connector for Equipment With Integrated Primary Protection (9.12.6)	44

Grounding Conductors in the EIPP (9.13.1)	45

Appendix A	47

- LIST OF TABLES

Page

Table 16-1: Bonding and Grounding Summary of Test Results	4

Table 16-2: DC Power Sources Detailed List of Test Equipment	35

Table 16-3: AC Power Sources Detailed List of Test Equipment	37

Table 16-4: DC Fault Test Detailed List of Test Equipment	40

Table 16-5: Frame EFT Test Detailed List of Test Equipment	41

Table 16-6: Frame Surge Test Detailed List of Test Equipment	42

Table 16-7: AC Fault Test Detailed List of Test Equipment	43

Table 16-8: Grounding Connector for Equipment With Integrated Primary Protection Test Detailed List of Test Equipment	44

- LIST OF FIGURES

Page

Error! No table of figures entries found.

## Summary of Test Results

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-1089-CORE.

- Section Name column gives the Section name from GR-1089-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-1089-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, Non-compliant, etc.).

- Compliant: The Equipment Under Test (<Product Name>) met the requirements of the corresponding criteria.

- Non-compliant: The <Product Name> did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to the <Product Name>.

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- For additional details, go to the page listed in this report.

- Page column gives the page number, in this report, for the corresponding criteria.

Table 16-1: Bonding and Grounding Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Comments | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 9. | Bonding and Grounding | - | - |  | - |
| 9.2 | General Requirements | R9-1 [75] |  |  | 8 |
| 9.3 | Equipment Grounding Systems | R9-2 [76] |  |  | 9 |
| 9.3.1 | The Common Bonding Network (CBN) | R9-3 [116] |  |  | 10 |
| 9.4 | AC Equipment Grounding | R9-4 [77] |  |  | 11 |
| 9.5 | Communication Equipment Grounding | R9-5 [213] |  |  | 13 |
| 9.5.1 | Network Telecommunications Facilities | R9-6 [78] |  |  | 14 |
| 9.5.2 | Locations Where the NEC Applies | R9-7 [146] |  |  | 16 |
| 9.5.3 | Outside Plant | R9-8 [147] |  |  | 17 |
| 9.6 | Unit Bonding and Grounding | R9-9 [79] |  |  | 18 |
| 9.7 | Provisions for Unit Assembly Bonding and Grounding | R9-10 [148] |  |  | 19 |
| 9.7.1 | Connectors and Connection Methods for Equipment Unit Assemblies | R9-11 [149] |  |  | 21 |
| 9.7.2 | Bonding of Circuit Packs | R9-12 [150] |  |  | 23 |
| 9.8 | DC Power System Grounding | - | - |  | - |
| 9.8.1 | Centralized Power Sources | R9-13 [80] |  |  | 24 |
| 9.8.2 | Embedded Power Sources | R9-14 [81] |  |  | 25 |
| 9.8.3 | Bonding of Battery Return (BR) Input Terminals | R9-15 [151] |  |  | 27 |
|  |  | R9-16 [152] |  |  | 27 |
| 9.9 | Bonding and Grounding Conductor and Connection Requirements | - | - |  | - |
| 9.9.1 | Bonding and Grounding Conductors | R9-17 [82] |  |  | 29 |
| 9.9.2 | Connections | R9-18 [83] |  |  | 30 |
|  |  | R9-19 [84] |  |  | 30 |
|  |  | R9-20 [85] |  |  | 30 |
|  |  | R9-21 [86] |  |  | 30 |
|  |  | R9-22 [87] |  |  | 30 |
|  |  | R9-23 [88] |  |  | 30 |
| 9.9.3 | Connectors | R9-24 [89] |  |  | 32 |
|  |  | R9-25 [90] |  |  | 32 |
|  |  | R9-26 [91] |  |  | 32 |
| 9.10 | Short Circuit Tests | - | - |  | - |
| 9.10.1 | DC Power Sources | R9-27 [92] |  |  | 33 |
| 9.10.2 9.12 | AC Power Sources Compatibility of Former IBN Equipment with CBN Currents | R9-28 [93] |  |  | 36 |
|  |  | - | - |  | - |
| 9.12.1.7 | Test Environment | CR9-29 [117] |  |  | 38 |
| 9.12.2 | Identification of Test Points | R9-30 [118] |  |  | 39 |
| 9.12.3 | DC Fault Test | CR9-31 [119] |  |  | 40 |
| 9.12.4 | Frame EFT Test | CR9-32 [121] |  |  | 41 |
| 9.12.5 | Frame Surge Test | CR9-33 [122] |  |  | 42 |
|  |  | CO9-34 [123] |  |  | 42 |
| 9.12.6 | AC Fault Test | CR9-35 [120] |  |  | 43 |
| 9.13 | Grounding Connector for Equipment With Integrated Primary Protection | R9-36 [214] |  |  | 44 |
|  |  | R9-37 [215] |  |  | 44 |
| 9.13.1 | Grounding Conductors in the EIPP | R9-38 [216] |  |  | 45 |
|  |  | R9-39 [217] |  |  | 45 |

## Overview

### Project Objective

Testing was performed to determine if the <Product Name> met the requirements for Section 9, Bonding and Grounding, of Telcordia Technologies GR-1089-CORE, Issue 6, May 2011.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

## General Requirements Principles (9.2)

### Criteria:

R9-1 [75]	A bonding and grounding system shall employ electrical conducting paths intentionally provided for the purpose. Bonds within and between frames, cabinets, and other metallic structures shall be specifically provided. The bonding and grounding system shall not depend on incidental paths such as those existing between chassis and frames, cable rack sections, and building steel sections.

Conductive objects with accessible surface areas of less than 100 mm2 that are not likely to become energized are not required to be grounded.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-1 [75].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Grounding Systems (9.3)

### Criteria:

R9-2 [76]	The equipment documentation and installation instructions shall indicate whether the EUT is suitable for installation as part of the Common Bonding Network (CBN) or an Isolated Bonding Network (IBN) or both.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-2 [76].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Common Bonding Network (CBN) (9.3.1)

### Criteria:

R9-3 [116]	Equipment having multiple intentional or incidental connections to the CBN (bonded as part of a CBN) and that has previously been required to be bonded in an IBN shall comply to the requirement of Section 9.12.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-3 [116].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## AC Equipment Grounding (9.4)

### Criteria:

R9-4 [77]	Requirements of Article 250 of the most recent edition of the National Electrical Code (NEC), ANSI/NFPA 70,[49] shall be met except where superseded by local electrical codes. Also, in network telecommunication facilities, all AC-operated equipment and AC system components shall be grounded as follows.

• All ac feeder and branch-circuit conductors shall be run in metallic raceway from source to load. The raceway shall be joined to form an electrically continuous equipment grounding conductor.

• An Alternating Current Equipment Grounding (ACEG) conductor, enclosed in the same raceway with the phase conductors, shall be provided for circuits distributing ac power. This conductor shall be solid or stranded, insulated, covered, or bare, and when covered or insulated, it shall be identified by a continuous green color or a continuous green color with one or more yellow stripes. All ACEG conductors shall be bonded to each junction box that they pass through and shall terminate on the enclosure of the equipment being powered or on the junction box containing the load being served.

• ACEG conductors (sometimes referred to as the “green wire” ground) shall be made of the same metal that is used for their associated phase and neutral conductors (copper or aluminum). The size of the ACEG shall be in accordance with Section 250.122 of the most recent issue of the NEC.

• Armored cable containing a bare bonding strip to decrease sheath resistance shall not be used as an equipment grounding conductor. Armored cable may be used if a separate equipment grounding conductor is contained within the armor.

• All ac distribution raceways and enclosed ACEG conductors that enter IBN equipment area shall be bonded to the main ground bus within the ground window associated with that IBN.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-4 [77].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Communication Equipment Grounding (9.5)

### Criteria:

R9-5 [213]	The equipment documentation and installation instructions shall indicate whether the EUT is suitable for installation in one or more of the following:

• Network Telecommunication Facilities

• Locations where the NEC applies

• OSP.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-5 [213].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Network Telecommunication Facilities (9.5.1)

### Criteria:

R9-6 [78]	Frames, cabinets, and metallic enclosures of communication equipment shall be grounded as follows.

• A Central Office Ground (CO GRD) system shall be provided in each CO according to practices specified by the telecommunications service provider. Similarly, in CEVs, EEEs, and similar facilities, an interior equipment grounding system shall be provided according to practices specified by the telecommunications service provider.

• The CO GRD system, or interior equipment grounding system, shall be connected to a building grounding electrode system approved by the telecommunications service provider.

• Distributing frames and protector frames shall be grounded as part of the CBN.

• Each frame, cabinet, or similar metallic communication equipment enclosure or supporting assembly shall provide a means for attaching a connector to be used for making the connection to the CO GRD system or interior equipment grounding system. The location for the attaching means shall be readily accessible to the installer. The connector shall be installed in accordance with the requirements described in Section 9.9.2 and Section 9.9.3.

NOTE: Requirements for interfacing electronic Stored Program Control Switching Systems with the CO GRD system and with CO power systems are contained in GR-295-CORE.[1]

• To minimize possible differences of potential, all CBN conductive elements located within 6 feet of an IBN shall be bonded to the IBN main ground bus within the ground window. Such elements include, but are not limited to

— Metallic stands and desks

— Electromechanical equipment frames

— Ironwork

— Lighting fixtures that are not part of the IBN

— Air ducts.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-6 [78].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Locations Where the NEC Applies (9.5.2)

### Criteria:

R9-7 [146]	At locations where applicable, requirements of the most recent edition of the NEC, Article 800 or Article 830, as applicable, covering listing requirements for equipment intended to be electrically connected to a telecommunications network shall be met. Equipment grounding requirements as specified in the equipment listing shall be met.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-7 [146].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Outside Plant (9.5.3)

### Criteria:

R9-8 [147]	For network telecommunications equipment installed in the OSP, an attachment means shall be available for connecting to the metallic equipment enclosure or to non-current-carrying metallic equipment frames, a No. 6 AWG copper grounding conductor from an approved grounding electrode. Non-current carrying metallic parts of network equipment installed in the OSP shall be grounded in accordance with Rule 99 of the most recent edition of the National Electrical Safety Code (NESC), ANSI/IEEE C2. [51]

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-8 [147].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Unit Bonding and Grounding (9.6)

### Criteria:

R9-9 [79]	An electrical conducting path shall exist between a unit's chassis and the metalwork of the enclosure in which it is mounted or a grounding conductor. Electrical continuity shall be provided by at least one of the following methods:

• Separate conductor(s) between the unit's chassis and the enclosure metalwork or a nearby point on the CO GRD system or the interior equipment grounding system.

— For units installed in an IBN, the requirements of GR-295-CORE [1]  apply.

• The use of thread-forming type unit mounting screws that remove any paint or nonconductive coatings and establish metal-to-metal contact. Suppliers’ documentation shall require that paint and other nonconductive coatings be removed on the surfaces between the mounting hardware and the framework or cabinet. The documentation shall also require the surfaces to be cleaned and an anti-oxidant applied before being joined.

This path shall be of sufficiently low impedance to facilitate the operation of any circuit over-current protection and it shall be capable of safely conducting any fault current likely to be imposed. This includes fault current from sources within the unit, such as dc-to-dc converters. Tests shall be performed in accordance with the requirements in Section 9.10.1 and Section 9.10.2.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-9 [79].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Provisions for Equipment Unit Assembly Bonding and Grounding (9.7)

### Criteria:

R9-10 [148]	Unit assemblies located in a network facility shall have an electrical conducting path provided on the assembly for adequately bonding exposed conductive surfaces and fault current carrying paths to a suitable grounding means. This suitable grounding means may be the supporting metalwork of the chassis, frame or cabinet or a ground terminal that can be grounded in accordance with Section 9.6 or Section 9.5.

NOTE: UL 60950 and IEC 60950 use the term “protective earthing terminal” to refer to such suitable grounding means.

Electrical continuity shall be provided by the following method.

• Exposed conductive surfaces, (e.g., conductive faceplates of circuit packs) must be intentionally bonded to the grounding means of the unit. The bonding of exposed conductive surfaces to the grounding means must have a sufficiently low impedance (<100 mΩ) to adequately carry fault currents and prevent unsafe voltage potentials.

—  In particular, doors or covers on equipment that are intended to remain attached to the equipment assemblies during maintenance shall be bonded with an appropriate gauge stranded wire or copper braid wire and attached with anti-rotation connection methods (e.g., barriers, lock-washers).

• The conducting path from the exposed conductive surfaces shall be of sufficiently low impedance (<100mΩ) to facilitate the operation of any circuit over-current protection and it shall be capable of safely conducting any fault current likely to be imposed. This includes fault currents from sources within the equipment, such as dc-dc converters. Tests shall be performed in accordance with the requirements in Section9.10.1 and Section9.10.2.

• Exposed surfaces for shielded or coaxial cable connectors are not required to be solidly bonded under the following conditions:

- The connector belongs to the receive port of transmission circuit that has a defined transmit and receive end

- Manufacturer’s instructions state that the transmit end of the cable must be grounded

- The circuit does not contain sources at Class A3 or higher as defined in Section 7

—  The connector is not likely to become energized with other sources within the equipment.

Exposed surfaces for shielded or coaxial cable connectors for the transmit end or where the transmit or receive ends cannot be identified shall be bonded as required in this section.

NOTE: Painted surfaces are considered conductive in terms of accessibility as thickness, porosity, and dielectric strength of paint are not controlled. Painted surfaces are not considered conductive for electrical connections.

NOTE: Conductive objects with accessible surface areas of less than 100mm2 that are not likely to become energized, are not required to be grounded.

NOTE: Extractor tabs or faceplate latches need not be grounded provided an investigation determines it is unlikely that they could become energized as a result of normal operation or a reasonable fault.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-10 [148].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Connectors and Connection Methods for Equipment Unit Assemblies (9.7.1)

### Criteria:

R9-11 [149]	Connectors and connection methods for bonding and grounding equipment assemblies shall meet the following requirements:

• Grounding connectors on equipment assemblies shall be NRTL listed or recognized for the purpose and shall be compatible with bonding and grounding conductors specified in Section 9.9.1. Ground studs or other integrated ground connection means are acceptable on equipment provided the equipment is listed and is capable of terminating a grounding conductor in a manner consistent with this section.

• Two-hole connectors shall not be required on smaller subassemblies (e.g., circuit pack shelves and magazines) contained within cabinets, frames, and racks where anti-rotation devices (e.g., barriers, lockwashers) are used or where there is minimal possibility of loosening from rotation during installation and maintenance activity.

• A soldering lug, screwless (push-in wire) connector, or a quick-connect or other friction-fit connector shall not be used to terminate a bonding or grounding conductor to the suitable grounding means.

• Connection devices or fittings for the suitable grounding means that depend solely on solder shall not be used.

• Multiple bonding or grounding connectors shall not be secured by the same bolt and shall not need to be removed to perform other service or installation procedures. It is permissible to connect other bonding or grounding conductors to a grounding connector provided a reliable bond between the connector and the equipment is not disturbed during installation, service or maintenance.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-11 [149].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Bonding of Circuit Packs (9.7.2)

### Criteria:

R9-12 [150]	Circuit packs/modules that plug into equipment assemblies and that contain parts that require grounding, shall be bonded to the host system's grounding means either by intentional and reliable metal-to-metal contact or by wires, PCB traces, appropriate backplane connectors or similar means.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-12 [150].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Centralized Power Sources (9.8.1)

### Criteria:

R9-13 [80]	In network telecommunication facilities, all centralized dc power systems (those not embedded within the equipment being powered) shall be grounded to the CO GRD system, to the facility's interior equipment grounding system or both. The required grounding shall consist of connecting the return side (usually the positive terminal) of the centralized power source to the CO GRD system, the interior equipment grounding system or both. For power sources supplying IBN loads such as electronic SPCSS, the return side of the power source shall be grounded in accordance with the requirements of GR-295-CORE.[1]

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-13 [80].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Embedded Power Sources (9.8.2)

### Criteria:

R9-14 [81]	Embedded dc power sources shall be grounded except as noted in the following clause:

- Embedded dc power sources with a rated output of 150VA or less and containing output power limiting (e.g., “fold-back” output V-I characteristic), and conforming to the short-circuit requirements of Section9.10.1, need not be grounded. Where multiple sources have parallel outputs, the rated output is considered to be the sum of the rated outputs of all individual sources that are in parallel.

- Embedded dc power sources with outputs rated greater than 150VA in products intended to comply with the requirements IEEE Std. 802.3af-2003[52] shall not be grounded provided they comply with all of the following:

  - The embedded source does not supply power to any loads outside the equipment enclosure without additional power limitation. If power derived from this embedded power source is distributed outside the enclosure, it shall comply with the power limitation requirements of Section 7.6.

  - The embedded source output is connected to ground through a capacitance or provided with a grounded screen between input and output.

  - The source provides output power limiting (e.g., “fold-back” output V-I characteristic) and conforms to the short-circuit requirements of Section 9.10.1.

- Embedded dc power sources with outputs rated greater than 150VA shall not be grounded provided they comply with all of the following:

  - The embedded source supplies power greater than 150VA solely to equipment shelf, circuit packs, or module where it is mounted. Any power supplied to loads outside this equipment shelf, circuit packs, or module shall be limited to 150VA for any non-capacitive load measured after one second of operation with any overcurrent protection bypassed.

  - The source provides output power limiting (e.g., “fold-back” output V-I characteristic) and conforms to the short-circuit requirements of Section 9.10.1.

The required grounding shall consist of connecting the output terminal that is designated to be grounded to one of the following:

- The equipment frame (see Figure 9-1A).

- A ground bus, backplane layer, or other connection means that is bonded to the equipment frame.

- A designated terminal that may be located outside of the equipment frame. • This designated terminal shall be connected to the CO GRD system and bonded to each frame that it serves. The bonding to the frames could be by a direct connection or by connecting to a CO GRD terminal used as a bonding terminal for the frames. (See Figure9-1B).

- To the BR conductor in the EUT directly or indirectly (See Figure 9-1C).

To the greatest extent practicable, the grounding location should be at the immediate output of the power source. Grounding at the load or between the immediate output and the load is permitted as necessary.

Embedded power sources located within IBN equipment frames shall be grounded in accordance with GR-295-CORE.[1]

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-14 [81].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Bonding of Battery Return (BR) Input Terminals (9.8.3)

### Criteria:

R9-15 [151]	If the equipment has a dc power port, the equipment documentation and installation instructions shall specify the treatment of the Battery Return (BR) input terminals as one of the following

• Isolated DC return (DC-I),

• Common DC return (DC-C), or

• Either DC-C or DC-I.

In the DC-I configuration, the DC return terminal or conductor is not connected to the equipment frame or the grounding means of the equipment. In the DC-C configuration, the BR terminal or conductor is connected to the equipment frame or to the grounding means of the equipment.

Equipment in a DC-I configuration shall not have any solid connections within the equipment between the BR and frame, or between the BR and the grounding means of the equipment. Filters shall be permitted to be installed between the DC input and frame. In this case, the total current conducted by all filters of the equipment unit (see Section 9.6) into the frame and the grounding means shall not exceed X*3.5 milliamperes (DC or 60-Hz AC), where X is the total number of dc power terminals (-48V and BR). This current shall be measured by isolating the EUT from ground (except the grounding conductor), and measuring the current in the grounding conductor with the EUT fully powered. The BR of the power source shall be connected to ground during the measurements.

Tests for all the criteria of this GR shall be performed with the equipment in the specified DC-return configuration. For the equipment compatible with the DC-C or DC-I configuration, the conducted immunity tests on the DC power leads shall be done in both configurations. For other tests in this GR, the configuration of lowest impedance shall be used. Also see Section 3.4.4.8.5, Section3.5.5.3.5, and Section4.6.2.3. During the performance of the tests, the grounding and bonding conductor for the EUT and the associated power source shall not be any longer than necessary and shall avoid unnecessary bends and loops.

R9-16 [152]	In the DC-C configuration, the ampacity of the conductor connecting the equipment frame to the BR conductor shall be equal to or greater than the ampacity of the associated BR conductor.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R9-15 [151] and R9-16 [152].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Bonding and Grounding Conductors (9.9.1)

### Criteria:

R9-17 [82]	Bonding and grounding conductors shall be of sufficiently low impedance to facilitate the operation of circuit over-current protection devices and shall be capable of safely conducting any fault current likely to be imposed. Bonding and grounding conductors shall be made of copper (tinned or un-tinned). Aluminum conductors shall not be used. Conductors made of wire, bus bar, or braided strap are acceptable. Conductors can be either insulated or uninsulated.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-17 [82].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Connections (9.9.2)

### Criteria:

R9-18 [83]	Because of different characteristics of copper and aluminum, connection devices shall be properly installed and used. Conductors of dissimilar metals shall not be intermixed in a terminal or splicing connector where physical contact occurs between dissimilar conductors (such as copper and aluminum, or copper and copper-clad aluminum), unless the device is suitable for the purpose and conditions of use. Materials such as fluxes, inhibitors, and compounds, where employed, shall be suitable for the use, and shall be of a type that will not adversely affect the conductors, installation, or equipment.

R9-19 [84]	Bare conductors shall be coated with an appropriate antioxidant compound before crimp connections are made. All unplated connectors, braided strap, and bus bars shall be brought to a bright finish and then coated with an antioxidant before they are connected. Tinned, solder-plated, or silver-plated connectors and other plated connection surfaces do not have to be prepared in this manner, but they shall be clean and free of contaminants. All raceway fittings shall be tightened to provide a permanent low-impedance path.

R9-20 [85]	Multiple connectors shall not be secured by the same bolt assemblies.

R9-21 [86]	Unplated connection surfaces that are to be intentionally joined to form a bonding or grounding path shall be brought to a bright finish and then coated with an antioxidant before they are joined (electrically connected).

R9-22 [87]	Listed fastening hardware shall be compatible with the materials being joined and shall preclude loosening, deterioration, and electrochemical corrosion of the hardware and joined materials.

R9-23 [88]	Nonconductive coatings (such as paint, lacquer, and enamel) on equipment to be bonded or grounded shall be removed from threads and other contact surfaces to assure electrical continuity.

The use of thread-forming type unit mounting screws that remove any paint or nonconductive coatings and establish metal-to-metal contact as allowed in Section 9.8 is an acceptable means to meet this requirement.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R9-18 [83], R9-19 [84], R9-20 [85], R9-21 [86], R9-22 [87], and R9-23 [88].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Connectors (9.9.3)

### Criteria:

R9-24 [89]	Only listed two-hole compression-type connectors shall be used in making connections to flat surfaces (such as bus bars, frames, racks, or cabinets). Torquing and bolt assembly requirements for securing the connector shall be as specified by the connector supplier.

R9-25 [90]	Grounding and bonding conductors shall be connected (including tap connections) by exothermic welding or listed compression-type connectors to the greatest extent practicable. Where exothermic welding or listed compression-type connectors cannot be used, listed pressure connectors, listed clamps, or other listed means may be used. Connection devices or fittings that depend solely on solder shall not be used.

R9-26 [91]	A soldering lug, a screwless (push-in) connector, or a quick-connect or other friction-fit connector shall not be used to terminate a bonding or grounding conductor.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R9-24 [89], R9-25 [90], and R9-26 [91].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## DC Power Sources (9.10.1)

### Criteria:

R9-27 [92]	Except as noted below, at least one short-circuit test shall be performed on each type of dc power source having a rated power rating of > 15 VA associated with the network equipment. Typical types of dc supplies are rectifiers, rectifiers and associated battery, and dc-to-dc converters.

The short-circuit test need not be applied for a source consisting of a battery or a string of batteries that is not equipped with an overcurrent protective device. If the output of a rectifier or similar source is normally connected in parallel with batteries, the batteries shall be disconnected during the fault current tests on this source.

The short-circuit tests need not be applied for a source that solely provides power to a single telecommunications port if an equivalent short-circuit would be performed in accordance with Section 4.6.1.1.

These tests shall verify that the fault-current path will safely conduct the fault current resulting from the short circuit, that the grounding and bonding connections can withstand the fault current, and in the case of power supplies required to be grounded (R9-8 [147], R9-9 [79]), shall verify that the supplies are solidly grounded. Short circuits shall be initiated as follows:

• For grounded power supplies, short circuits shall be initiated between the ungrounded side of the source and the return conductor, and between the ungrounded side of the source and the metalwork of the enclosure. The short circuit shall first be initiated at the power supply output terminals, and repeated at the load if the load is remote from the power supply output terminals.

• For ungrounded power supplies with output ≤ 150 VA, the short circuit shall be initiated between the positive and negative output terminals. The short circuit

shall first be initiated at the power supply output terminals, and repeated at the load if the load is remote from the power supply output terminals. Supplies that have one of its outputs connected to the BR conductor directly or indirectly are considered grounded.

• For ungrounded  power supplies with output > 150 VA as permitted in R9-14 [81], the short circuit shall be initiated between the positive and negative output terminals. In addition, two separate short circuits between the positive and negative output terminals of one or more supplies and the metalwork of the enclosure shall be initiated. The short circuit(s) shall first be initiated at the power supply output terminals, and repeated at the load if the load is remote from the power supply output terminals.

Suggested points to initiate the short circuits are at points on the output circuit that are farthest from the source and downstream from over-current devices intended to protect equipment and wiring.

Short-circuit tests shall be applied to embedded dc power supplies that are mounted on (on-board) and intended to power individual circuit packs, as well as to supplies intended to power a complete shelf or rack of circuit packs. For on-board power supplies, the short circuit shall first be applied at the power supply output terminals, and repeated downstream (within the circuit pack) from the power supply output. A representative sample of test points shall be chosen to cover variations in wiring path lengths and affected components.

Where the architecture includes a separate power supply for an entire shelf or rack of circuit packs, the short shall first be applied at the output terminals of the power supply, and repeated at a point within the individual circuit pack(s) being powered. If there are a number of circuit pack types or configurations, then a representative sample of each type or configuration shall be tested.

For both grounded and ungrounded power supplies, conformance to this requirement shall be demonstrated by the following conditions.

• The EUT shall not become a fire, fragmentation, or electrical safety hazard as described in Section 4.

• There shall be no damage to or interruption of any bonding or grounding conductor or connector required in Section 9.5, Section 9.6, Section 9.7, and Section 9.8.

• The circuit pack, module, or subassembly where the short-circuit is applied, including any power supplies within the unit assembly, need not be in full working order after the short-circuit is removed. Damage to other circuit cards, modules, and subassemblies within the unit assembly shall not occur. Damage to other equipment or wiring shall not occur. Fuse replacement is permitted.

• A power supply that supplies multiple units shall be restorable by operator intervention (e.g., fuse replacement) after the removal of the short-circuit, except where the short is applied upstream of the protective circuit for the power supply.

Each short circuit shall be applied for one minute. When the supply ceases delivering current (e.g., overcurrent protection operates) the short circuit can be removed. If after one minute, the supply continues to deliver non-negligible (>1A) current into the short circuit, the short circuit shall be maintained until the current ceases or for 15 minutes, whichever occurs first.

If the circuit is interrupted by the opening of a component other than a Listed or Recognized overcurrent protection device, the test shall be repeated twice using new components as necessary.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-27 [92].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 16-2: DC Power Sources Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## AC Power Sources (9.10.2)

### Criteria:

R9-28 [93]	At least one short-circuit test shall be performed on each type and size of ac output supply associated with the network equipment. Supplies typically tested are dc-to-ac inverters and isolating transformers. The test shall determine

• Whether the fault-current path will safely conduct the fault current produced by the short circuit,

• Whether the grounding and bonding connections can withstand the fault current,

• Whether adequate short-circuit current is available to safely operate an overcurrent protective device, and whether the interrupting capacity rating of the overcurrent protective device is adequate, or

• Whether the foldback characteristics of the ac supply are adequate.

The short circuit shall be caused from phase to phase (if two or more phases are present), phase to neutral, and phase to grounded enclosure metalwork. Suggested test locations are at points on the output circuit that are farthest from the source.

For power supplies having output ratings of 500 VA or less, one of the following conditions must be met:

a. Fuse or circuit breaker shall operate to clear the fault in 0.5 second or less,

or

b. If the power source has a foldback volt-ampere characteristic, the output current shall reach its minimum value with the output voltage less than or equal to 0.1 Volt in less than 0.5 second.

For power supplies having output ratings greater than 500 VA, one of the following conditions must be met:

a. A fuse or circuit breaker shall operate to clear the fault in about 0.1 second,

or

b. If the power source has foldback Volt-Ampere characteristics, the output current shall reach its minimum value with the output voltage less than or equal to 0.1 Volt in less than 0.1 second.

Conformance with this requirement shall be demonstrated by the following conditions.

• The protective device shall operate or the foldback characteristics shall activate within the specified time.

• The EUT shall not become a fire, fragmentation, or electrical safety hazard as described in Section 4.

• There shall be no damage to or interruption of any bonding or grounding conductor or connector required in Section9.4, Section 9.5, Section 9.6, Section 9.7, and Section 9.8.

• The circuit pack, module, or sub-assembly where the short-circuit is applied, including any power supplies within the unit assembly, need not be in full working order after the short-circuit is removed. Damage to other circuit cards, modules, and subassemblies within the unit assembly shall not occur. Damage to other equipment or wiring shall not occur. Fuse replacement is permitted.

• A power supply that supplies multiple units shall be restorable by operator intervention (e.g., fuse replacement) after the removal of the short-circuit, except if the short is applied upstream of the protective circuit for the power supply.

If the circuit is interrupted by opening of a component other than a NRTL listed or recognized fuse, the test shall be repeated twice using new components as necessary.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R9-28 [93].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 16-3: AC Power Sources Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Test Environment - Compatibility of Former IBN Equipment with CBN Currents (9.12.1.7)

### Criteria:

CR9-29 [117]	The environment at the test site shall satisfy the following conditions.

1. Ambient Radio-Noise and Signals

Because large levels of ambient radio noise can cause EUT upset similar to that caused by the application of the tests in this section, it is desirable that the conducted and radiated ambient radio-noise and signal levels, measured at the test site with the EUT de-energized, be at least 6 dB below the allowable limit of the applicable limit or standard. However, the ambient radio noise level is not relevant if the EUT complies with the criteria of this section in the presence of this noise.

2. Temperature

The EUT and the measuring equipment should be within their normal operating temperature ranges.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Conditional Requirements CR9-29 [117].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Identification of Test Points - Compatibility of Former IBN Equipment with CBN Currents (9.12.2)

### Criteria:

R9-30 [118]	Test points shall be identified for application of test surges and connections to the reference ground plane. The set of test points shall include representative points where the manufacturer intends a connection between the EUT and CBN conductors. These include the point of connection to the following:

• ACEG conductor (if EUT is ac powered)

• Bonding conductors

• Communication conductors, e.g., cable shields, waveguides.

Where there are multiple identical connections to the CBN, such as several adjacent cable shields, only a single representative connection shall be chosen as a test point. The set of test points shall also include a sample of points where incidental connections to the CBN might occur, such as points of attachment to cable trays or other equipment frames.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R9-30 [118].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## DC Fault Test (9.12.3)

### Criteria:

CR9-31 [119]	The EUT shall not be damaged and shall continue to operate properly during testing in accordance with the following description and the circuit shown in Figure 9-2. The equipment case and the bonding connectors shall not suffer damage or exhibit arcing or overheating during the test. Service-affecting responses, unless within system operating limits, and manual interactions shall not occur. Section 2.1.3 provides a description of service-affecting responses and manual intervention.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Conditional Requirements CR9-31 [119].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 16-4: DC Fault Test Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Frame EFT Test (9.12.4)

### Criteria:

CR9-32 [121]	The EUT shall perform properly when an Electrical Fast Transient (EFT) at 4 kV is applied to each test point of the EUT. Service-affecting responses, unless within system operating limits, and manual interventions shall not occur. Section 2.1.3 provides a description of service-affecting responses and manual intervention.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/not compliant with Conditional Requirements CR9-32 [121].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 16-5: Frame EFT Test Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Frame Surge Test (9.12.5)

### Criteria:

CR9-33 [122]	The EUT shall not be damaged and shall continue to operate properly when subjected to a 3000A, 8/20s current surge applied to one of the test points of the EUT. The double exponential waveshape for the surge is defined in IEEE C62.41[30].

CO9-34 [123]	The EUT shall not be damaged and shall continue to operate properly when subjected to a 5000A, 8/20- s current surge applied to one of the test points of the EUT. The double exponential wave shape for the surge is defined in IEEE C62.41[30].

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/not compliant with Conditional Requirements CR9-33 [122] and CR9-34 [123].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 16-6: Frame Surge Test Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## AC Fault Test (9.12.6)

### Criteria:

CR9-35 [120]	The EUT shall perform properly during testing in accordance with the following paragraph and test circuit shown in Figure 9-7. The test shall be performed for a single representative AC receptacle or AC-powered circuit in each equipment cabinet. The equipment case and the bonding connectors shall not suffer damage or exhibit arcing or overheating during the test. Service-affecting responses, unless within system operating limits, and manual interventions shall not occur. Section2.1.3 provides a description of service-affecting responses and manual intervention.

Exception: AC-powered circuits where the fault test occurs and services that depend on these circuits need not be operational following the test.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Conditional Requirements CR9-35 [120].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 16-7: AC Fault Test Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Grounding Connector for Equipment With Integrated Primary Protection (9.12.6)

### Criteria:

R9-36 [214]	The primary protector and the unprotected circuit shall have a common bonding point or bar within the equipment enclosure. This common point shall be connected to the grounding means of the equipment. The grounding means of the equipment shall be sized for connection of No. 6 AWG copper grounding conductor.

R9-37 [215]	When terminated with a No. 6 AWG or larger solid or stranded copper wire, the ground connection means of the EUT shall be capable of carrying a 60-Hz sinusoidal current of 1500 A rms for 6 seconds without evidence of cracking, breaking or melting.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R9-36 [214] and R3-37 [215].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 16-8: Grounding Connector for Equipment With Integrated Primary Protection Test Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Grounding Conductors in the EIPP (9.13.1)

### Criteria:

R9-38 [216]	Unless fusing takes place on the EUT board, a discrete protector block shall be connected to the grounding means of the EUT using a grounding conductor not smaller than specified in Table 9-2.

Table 9-2 Grounding Conductor Size for Fuse-Less Protector Block in the EUT

| Number of Printed Circuits | Minimum Size of Grounding Conductor |
| --- | --- |
| 5 | 12 AWG |
| 6 | 10 AWG |
| 7 or more | 6 AWG |

R9-39 [217]	If fusing takes place on the EUT board, the board containing the protectors shall be connected to the grounding means of the EUT using a grounding conductor not smaller than specified Table 9-3.

Table 9-3 Grounding Conductor Size for Fused Protector Block in the EUT

| Number of Printed Circuits | Minimum Size of Grounding Conductor |
| --- | --- |
| 6 | 12 AWG |
| 7 | 10 AWG |
| 8 or more | 6 AWG |

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. signal and power cable dressing) from the NEBS Compliance Checklist which pertain to the electromagnetic compatibility and electrical safety criteria>>

<<State if testing to the GR-1089-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Conditional Requirements R9-38 [216] and R9-39 [217].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

<<Insert tables with detailed description of equipment pack fill>>