TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

Part 19

Equipment Spatial Design Requirements for Frames and Chassis

Section 3, GR-63-CORE

Telcordia Technologies GR-63, Issue 4, April 2012

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Page

Test Results Summary	3

Overview	5

Equipment Frame Nomenclature (3.1)	6

Equipment Frame Floor Mounting (3.2)	7

Equipment Frame Junctioning (3.3)	8

Equipment Frame Dimensioning (3.4)	9

Equipment Frame Dimensioning – Open Style Racks (3.4.1)	10

Equipment Frame Dimensions – Other Rack Styles (3.4.2)	11

Equipment Frame Dimensioning - Shipping (3.4.3)	12

Equipment Frame End Guards (3.4.4)	13

Equipment Frame Cable Management Provisions (3.5)	14

Equipment Frame Interface with Cable Rack (3.5.1)	15

Equipment Frame Support of CDS and Lights (3.7)	16

AC onvenience Outlets Within Equipment Frames (3.8)	17

Distributing Frames (3.9.1)	18

DC Power Plant Equipment Frames (3.10)	19

Equipment-Chassis Mounting Requirments (3.11)	20

Appendix A	21

- LIST OF TABLES

Page

Table 18-1: Spatial Requirements Summary of Test Results	3

- LIST OF FIGURES

Page

Error! No table of figures entries found.

## Test Results Summary

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-63-CORE.

- Section Name column gives the Section name from GR-63-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-63-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, Non-compliant, etc.).

- Compliant: The Equipment Under Test met the requirements of the corresponding criteria.

- Non-compliant: The Equipment Under Test did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to Equipment Under Test {Explanation Required}

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- Page column gives the page number, in this report, for the corresponding criteria.

Table 18-1: Facility and Space Planning Requirements Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Comments | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 3. | - Equipment Spatial Design Requirements for Frames and Chassis | - | - |  | - |
| 3.1 | Equipment Frame Nomenclature | R3-1 [5] |  |  | 6 |
| 3.2 | Equipment Frame Floor Mounting | R3-2 [1] |  |  | 7 |
|  |  | R3-3 [2] |  |  | 7 |
|  |  | R3-4 [180] |  |  | 7 |
|  |  | R3-5 [181] |  |  | 7 |
|  |  | R3-6 [6] |  |  | 7 |
| 3.3 | Equipment Frame Junctioning | R3-7 [182] |  |  | 8 |
| 3.4 | Equipment Frame Dimensioning | R3-8 [183] |  |  | 9 |
| 3.4.1 | Equipment Frame Dimensioning – Open Style Racks | O3-9 [14] |  |  | 10 |
|  |  | O3-10 [148] |  |  | 10 |
| 3.4.2 | Equipment Frame Dimensioning – Other Rack Styles | O3-11 [150] |  |  | 11 |
| 3.4.3 | Equipment Frame Dimensioning – Shipping | R3-12 [3] |  |  | 12 |
| 3.4.4 | Equipment Frame End Guards | R3-13 [17] |  |  | 13 |
| 3.5 | Equipment Frame Cable Management Provisions | R3-14 [151] |  |  | 14 |
|  |  | O3-15 [152] |  |  | 14 |
|  |  | O3-16 [184] |  |  | 14 |
| 3.5.1 | Equipment Frame Interface with Cable Rack | R3-17 [15] |  |  | 15 |
|  |  | O3-18 [16] |  |  | 15 |
|  |  | R3-19 [185] |  |  | 15 |
| 3.7 | Equipment Frame Support of CDS and Lights | R3-20 [186] |  |  | 16 |
| 3.8 | AC Convenience Outlets Within Equipment Frames | R3-21 [20] |  |  | 17 |
|  |  | R3-22 [21] |  |  | 17 |
| 3.9.1 | Distributing Frames (DFs) | O3-23 [187] |  |  | 18 |
|  |  | R3-24 [23] |  |  | 18 |
|  |  | O3-25 [188] |  |  | 18 |
| 3.10 | DC Power Plant Equipment Frames | R3-26 [189] |  |  | 19 |
|  |  | O3-27 [190] |  |  | 19 |
|  |  | O3-28 [191] |  |  | 19 |
| 3.11 | Equipment-Chassis Mounting Requirements | R3-29 [192] |  |  | 20 |
|  |  | O3-30 [149] |  |  | 20 |
|  |  | R3-31 [193] |  |  | 20 |

## Overview

### Project Objective

Testing was performed to determine if the <Product Name> met the requirements for Section 3, Equipment Spatial Design Requirements for Frames and Chassis, of GR-63-CORE, Issue 4, April 2012.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

## Equipment Frame Nomenclature (3.1)

### Criteria:

R3-1 [5]	No part of any frame or apparatus attached to the frame (including installed cables) shall extend horizontally beyond the front or rear edges of the base (or guardrail) of the frame. Frame-base extenders may be used to increase the effective base depth.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-1 [5].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Floor Mounting (3.2)

### Criteria:

R3-2 [1]	All equipment frames shall have a hole pattern on a flat horizontal surface on the base of the frame for anchoring to building floors.  The hole pattern shall permit lateral relocation of the fasteners to avoid interference with reinforcement bars.  Use Figure 3-2 as a guide.

R3-3 [2]	The frame base and anchoring method shall provide for a self-supporting equipment frame that can withstand overturning moments caused by cable-pulling or earthquake effects without auxiliary support or bracing from the ceiling or side walls. As a minimum, the floor anchoring method shall withstand the overturning load of a 450 N (100 lbf) applied at the top of the frame in any horizontal direction.

R3-4 [180]	Access to the anchoring hardware with electronics in place and operating shall be provided for verification that hardware continues to meet torque requirements.

R3-5 [181]	The equipment-base floor anchor bolt system shall be designed so the equipped framework can be fitted laterally into its space under an existing Cable Distribution System (CDS), and then secured to the building floor with appropriately sized anchors. See Section 4.4.2, “Framework and Anchor Criteria,” for concrete expansion anchor criteria.

R3-6 [6]	Means to level and plumb the frames and to compensate for variation in floor flatness, such as wedges, shims, or leveling screws, shall be part of, or available for, the frame.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-2 [1], R3-3 [2], R3-4 [180], R3-5 [181] and R3-6 [6].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Junctioning (3.3)

### Criteria:

R3-7 [182] 	Frames shall have provisions for junctioning to adjacent (i.e., side-to-side or back-to-back) frames. Junctioning shall connect upper structural portions of frames.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R3-7 [182].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Dimensioning (3.4)

### Criteria:

R3-8 [183] 	Suppliers shall provide scaled dimensional drawings of frames. At a minimum, drawings shall show overall dimensions, equipment chassis and base mounting details, junctioning locations and details, and cable rack/top support interface. Drawings shall be included in the NEBS testing report.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R3-8 [183].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Dimensioning – Open Style Racks (3.4.1)

### Criteria:

O3-9 [14] 	Open style equipment racks should have the following nominal overall dimensions:

| Height | Nominal 2130 mm (7 ft) |
| --- | --- |
| Width | Nominal 560 mm (23 in) for 19-inch equipment Nominal 660 mm (26 in) for 23-inch equipment |
| Depth | Nominal 300 mm (12 in) |

O3-10 [148] 	Open-style racks should not be used for products deeper than 600 mm (24 in) even when base extenders are used.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objectives O3-9 [14] and O3-10 [148].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Dimensions – Other Rack Styles (3.4.2)

### Criteria:

O3-11 [150] 	Equipment racks for newer equipment areas or to support deeper chassis should have the following nominal overall dimensions:

| Height | Nominal 2130 mm (7 ft) |
| --- | --- |
| Width | Nominal 600 mm (24 in), or Nominal 750 mm (30 in) |
| Depth | Nominal 600 mm (24 in), or Nominal 750 mm (30 in), or Nominal 900 mm (36 in) |

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O3-11 [150].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Dimensioning - Shipping (3.4.3)

### Criteria:

R3-12 [3] 	Any frame, when packaged for transit and accompanied or supported by the usual handling facilities, shall fit through typical equipment entrances 1219 mm (4 ft) wide and 2438 mm (8 ft) high.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R3-12 [3].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame End Guards (3.4.4)

### Criteria:

R3-13 [17] 	When end guards are provided for equipment frames, end guards for equipment frames shall be as wide as the equipment frames are deep and extend the full height of the frame.  The minimum aisle spacings must be maintained when the end guards are added to an equipment lineup.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R3-13 [17].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Cable Management Provisions (3.5)

### Criteria:

R3-14 [151] 	All framework shall provide access to permit cabling from top or bottom.

O3-15 [152] 	All framework should be manufactured to allow orderly placement of larger cables, i.e., power conductors, such that these do not interfere with access to equipment mounted in the framework, each other, or other cables routed into the framework.

O3-16 [184] 	Equipment frames should have provisions to segregate and separately route power cables from communication cables both within and exiting the frame. Segregation and routing should allow for the maintenance of common elements (fan filters, fan trays, power supplies, etc.) and the addition of new shelf hardware (circuit packs, Small Form-factor Pluggables [SFPs], etc.) without disturbing functioning cables.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R3-14 [151] and Objectives O3-15 [152] and O3-16 [184].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Interface with Cable Rack (3.5.1)

### Criteria:

R3-17 [15] 	Equipment frames shall be capable of supporting and providing a fastening arrangement for all system Cable Distribution Systems (CDSs).  The design of the interface between the frame and CDS shall permit the insertion or removal of a frame from an equipment lineup.  To permit this insertion or removal, a minimum clearance of 10 mm (0.39 in), except for spacers, shall normally be provided between the top of the frames and the bottom of the CDS.

O3-18 [16]	Framework top cross-member should provide the following fastenings:  a minimum of two 13-mm (0.51-in) diameter holes (with room for a nut) or two M10 (or 3/8 – 16) tap-through holes (with at least four full threads).  The holes shall be located on the longitudinal centerline and 121 mm (4.75 in) to either side of the front-to-back centerline of the framework top, as Figure 3-3 shows.

R3-19 [185]	Minimum bend radius for fiber cable shall be maintained during transitions from the cable rack to the equipment frame. At drop-off points, a bend radius support may be required.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-17 [15] and R3-19 [185] and Objective O3-18 [16].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Support of CDS and Lights (3.7)

### Criteria:

R3-20 [186] 	An equipment frame shall be able to support all overhead CDSs and lights located up to 3048 mm (10 ft) above the floor and having a maximum weight of 122.1 kg/m2 (25.0 lb/ft2). In partially equipped lineups, CDSs and lights may be partially supported by floor-mounted stanchions. Over unequipped areas, via CDSs, (defined in Section 2.6) may be supported by stanchions or from the ceiling.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-20 [186].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## AC onvenience Outlets Within Equipment Frames (3.8)

### Criteria:

R3-21 [20] 	The base of each frame, behind the front and rear guardrails, shall have space for ac power distribution for convenience outlets.  The sides of the frame base must be sufficiently open or have holes that permit distribution wire to run through the frames.  The front and rear of the frame base and/or guardrail shall provide the means and location for convenience outlets.  When design control for a system includes the end guards at both ends of a lineup, the convenience outlets may be located in the end guards instead of in the base of each individual frame.

R3-22 [21]	Alternating current power distribution for connecting outlets or lighting fixtures that may be part of the frame assembly shall be designed and constructed to comply with the National Electrical Code (NEC), except where those requirements are superseded by applicable local electrical and building codes.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-21 [20] and R3-22 [21].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Distributing Frames (3.9.1)

### Criteria:

O3-23 [187] 	DFs should have a maximum height of 2743 mm (9 ft) including associated system cabling, which includes all terminating cabling and racks.

R3-24 [23]	Frames shall have a maximum floor load of 659 kg/m2 (135.0 lb/ft2).  This uniform load is the total weight of all distributing frame equipment in the area, including cabling and racks, divided by the associated floor area, including aisles.  When such areas exceed 37.2 m2 (400 ft2), any 6.1-m by 6.1-m portion (20-ft by 20-ft), regardless of its location relative to the columns, should not exceed the floor load requirement.

O3-25 [188]	DFs should be capable of supporting all overhead CDSs and lights. (In partially equipped lineups, cabling and lights may be supported by floor-mounted stanchions.).

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-24 [23] and Objectives O3-23 [187] and O3-25 [188].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## DC Power Plant Equipment Frames (3.10)

### Criteria:

R3-26 [189] 	The height of centralized dc power plant equipment, including all superstructure and overhead facilities such as cable, cable racks and bus bars, shall not exceed 3048 mm (10 ft). This vertical space allocation also includes and vertical clearance (headroom) necessary for installation, operation, and maintenance. Figure 3-4 shows a typical centralized dc power plant equipment area.

O3-27 [190]	Centralized dc power equipment frames should be capable of being installed on building floor structures having a total floor load capacity of 732 kg/m2 (150.0 lb/ft2). Centralized dc power plant frames are allocated 684 kg/m2 (140.0 lb/ft2) with 8.8 kg/m2 (10.0 lb/ft2) allocated for transient loads..

O3-28 [191]	Centralized dc power plant equipment should support all overhead CDSs, bus bars and lights. (In partially equipped areas, these elements may be supported by floor-mounted stanchions.) Centralized dc power plant equipment shall be designated for base-mounted attachment to the floor without auxiliary support or bracing from the ceiling or side walls. When so supported, centralized dc power plant equipment shall be capable of withstanding the network environments, including earthquake environments, that Section 4.4 “Earthquake, Office Vibration and Transportation Vibration” describes.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-26 [189] and Objectives O3-27 [190] and O3-28 [191].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment-Chassis Mounting Requirments (3.11)

### Criteria:

R3-29 [192] 	Equipment chassis and associated mounting hardware shall utilize holes or closed slots for attachment to equipment frame mounting surfaces. See Figure 3-4.

O3-30 [149]	For chassis depths greater than or equal to nominal 450 mm (18 in), provisions to fasten the chassis to both front and rear faces of the rack mounting flange are desirable.

R3-31 [193]	Circuit packs shall be physically retained in place within a chassis or frame by a positive locking mechanism.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R3-29 [192] and R3-31 [193] and Objective O3-30 [149].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

<<Insert tables with detailed description of equipment pack fill>>