TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

Part 20

temperature, humidity and altitude

Section 4.1, GR-63-CORE

Telcordia Technologies GR-63, Issue 4, April 2012

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Page

Test Results Summary	3

Overview	5

Environmental Criteria  (4.0)	6

Low-Temperature Exposure and Thermal Shock (4.1.1.1)	7

High Relative Humidity Exposure (4.1.1.2)	8

High-Temperature Exposure and Thermal Shock (4.1.1.3)	9

Operating Temperature and Humidity Criteria (4.1.2)	10

Altitude (4.1.3)	12

Temperature Margin Evaluation (4.1.4)	13

Equipment Fan-Performance Criteria (4.1.5.1)	15

Equipment Fan-Filter Criteria (4.1.5.2)	17

Heat Dissipation and Energy Efficiency (4.1.6)	19

Surface Temperature (4.1.7)	21

Equipment Airflow (4.1.8)	23

Appendix A	24

- LIST OF TABLES

Page

Table 20-1: Temperature, Humidity, and Altitude Criteria Summary of Test Results	3

Table 20-2: Low Temperature Exposure and Thermal Shock Detailed List of Test Equipment	7

Table 20-3: High Temperature Exposure and Thermal Shock Detailed List of Test Equipment	8

Table 20-4: High Relative Humidity Exposure Detailed List of Test Equipment	9

Table 20-5: Operating Temperature and Humidity Detailed List of Test Equipment	11

Table 20-6: Altitude Detailed List of Test Equipment	12

Table 20-7: Temperature Margin Evaluation Detailed List of Test Equipment	14

Table 20-8: Fan Cooled Equipment Criteria Detailed List of Test Equipment	16

Table 20-9: Heat Dissipation Detailed List of Test Equipment	18

Table 20-10: Surface Temperature Detailed List of Test Equipment	20

Table 20-11: Equipment Airflow Detailed List of Test Equipment	21

- LIST OF FIGURES

Page

Error! No table of figures entries found.

## Test Results Summary

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-63-CORE.

- Section Name column gives the Section name from GR-63-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-63-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, Non-compliant, etc.).

- Compliant: The Equipment Under Test met the requirements of the corresponding criteria.

- Non-compliant: The Equipment Under Test did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to Equipment Under Test {Explanation Required}

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- Page column gives the page number, in this report, for the corresponding criteria.

Table 20-1: Temperature, Humidity, and Altitude Criteria Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Comments | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 4.0 | Environmental Criteria | R4-1 [67] |  |  | 6 |
|  |  | R4-2 [68] |  |  | 6 |
| 4.1 | Temperature, Humidity, and Altitude Criteria | - | - |  |  |
| 4.1.1 | Transportation and Storage Environmental Criteria | - | - |  |  |
| 4.1.1.1 | Low-Temperature Exposure and Thermal Shock | R4-3 [69] |  |  | 7 |
| 4.1.1.2 | High Relative Humidity Exposure | R4-4 [71] |  |  | 8 |
| 4.1.1.3 | High-Temperature Exposure and Thermal Shock | R4-5 [70] |  |  | 9 |
| 4.1.2 | Operating Temperature and Humidity Criteria | R4-6 [72] |  |  | 10 |
| 4.1.3 | Altitude | R4-7 [74] |  |  | 12 |
|  |  | R4-8 [136] |  |  | 12 |
|  |  | R4-9 [75] |  |  | 12 |
|  |  | O4-10 [137] |  |  | 12 |
|  |  | O4-11 [76] |  |  | 12 |
| 4.1.4 | Temperature Margin Evaluation | R4-12 [153] |  |  | 13 |
| 4.1.5.1 | Fan Cooled Equipment Criteria | R4-13 [154] |  |  | 15 |
|  |  | R4-14 [155] |  |  | 15 |
|  |  | O4-15 [156] |  |  | 15 |
|  |  | R4-16 [157] |  |  | 15 |
|  |  | R4-17 [158] |  |  | 15 |
| 4.1.5.2 | Equipment Fan-Filter Criteria | R4-18 [138] |  |  | 17 |
|  |  | R4-19 [139] |  |  | 17 |
|  |  | R4-20 [176] |  |  | 17 |
|  |  | R4-21 [140] |  |  | 17 |
|  |  | R4-22 [141] |  |  | 17 |
|  |  | R4-23 [142] |  |  | 17 |
|  |  | R4-24 [143] |  |  | 17 |
|  |  | O4-25 [144] |  |  | 17 |
|  |  | R4-26 [145] |  |  | 17 |
|  |  | O4-27 [194] |  |  | 17 |
| 4.1.6 | Heat Dissipation and Energy Efficiency | R4-28 [77] |  |  | 19 |
|  |  | O4-29 [78] |  |  | 19 |
|  |  | O4-30 [195] |  |  | 19 |
|  |  | R4-31 [196] |  |  | 19 |
| 4.1.7 | Surface Temperature | O4-32 [79] |  |  | 21 |
|  |  | R4-33 [159] |  |  | 21 |
| 4.1.8 | Equipment Airflow | R4-34 [160] |  |  | 23 |
|  |  | 04-35 [161] |  |  | 23 |
|  |  | R4-37 [198] |  |  | 23 |
|  |  | R4-38 [199] |  |  | 23 |

## Overview

### Project Objective

Testing was performed to determine if the <Product Name> met the requirements of Section 4.1, Temperature, Humidity, and Altitude Criteria, of GR-63-CORE, Issue 4, April 2012.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

## Environmental Criteria  (4.0)

### Criteria:

R4-1 [67] 	The equipment manufacturer shall be responsible to perform a Root Cause Analysis (RCA) for each failure that occurs during NEBS product testing, even if subsequent retesting is successful. The RCA shall include an explanation of what failed, why it failed, and what corrective action was taken.

R4-2 [68]	Corrective action to the root cause problem shall be consistent with customers’ reliability/technical requirements. Identification information (e.g., manufacturing cut-in dates, serial numbers, product ID changes, order requirements, availability, etc.) for equipment incorporating the corrective action shall be provided in the RCA.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with R4-1 [67] and R4-2 [68].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Low-Temperature Exposure and Thermal Shock (4.1.1.1)

### Criteria:

R4-3 [69]	The packaged equipment shall not sustain any damage or deteriorate in functional performance after it has been exposed to the environment described in Table 4-1.

Table 4-1. Low-Temperature Exposure and Thermal Shock

| Temperature | Event | Duration/Rate of Change |
| --- | --- | --- |
| 23°C to -40°C (73°F to -40°F) | Temperature transition | 30°C/hour (54°F/hour) |
| -40°C (-40°F) | Temperature soak | 72 hour (minimum) |
| 40°C to 23°C (-40°F to 73°F) | Temperature transition | < 5 minutes |

- Any humidity (or uncontrolled humidity).

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with R4-3 [69].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-2: Low Temperature Exposure and Thermal Shock Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## High Relative Humidity Exposure (4.1.1.2)

### Criteria:

R4-4 [71] 	The packaged equipment shall not sustain any damage or deteriorate in functional performance after it has been exposed to the environment described in Table 4-2.

Table 4-2. High Relative Humidity Exposure

| Temperature | Relative Humidity | Event | Duration/Rate of Change |
| --- | --- | --- | --- |
| 23°C to 40°C (73°F to 104°F) | 50% RH | Temperature transition | 30°C/hr (54°F/hr) |
| 40°C (104°F) | 50% to 93% RH | Humidity transition | < 2 hr |
| 40°C (104°F) | 93% RH | Temperature/humidity soak | 96 hr |
| 40°C (104°F) | 93% to 50% RH | Humidity transition | < 2 hr |
| 40°C to 23°C (104°F to 73°F) | 50% RH | Temperature transition | 30°C/hr (54°F/hr) |

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant Requirement R4-4 [70].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-3: High Temperature Exposure and Thermal Shock Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## High-Temperature Exposure and Thermal Shock (4.1.1.3)

### Criteria:

R4-5 [70]	The packaged equipment shall not sustain any damage or deteriorate in functional performance after it has been exposed to the environment described in Table 4-3.

Table 4-3. High-Temperature Exposure and Thermal Shock

| Temperature | Event | Duration/Rate of Change |
| --- | --- | --- |
| 23°C to 70°C (73°F to 158°F) | Temperature transition | 30°C/hour (54°F/hour) |
| 70°C (158°F) | Temperature soak | 72 hr (minimum) |
| 70°C to 23°C (158°F to 73°F) | Temperature transition | < 5 minutes |

- Any humidity (or uncontrolled humidity).

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R4-5 [71].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-4: High Relative Humidity Exposure Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Operating Temperature and Humidity Criteria (4.1.2)

### Criteria:

R4-6 [72]	The equipment shall not sustain any damage or deterioration of functional performance during its operating life when operated within the conditions of Table 4-4.

Table 4-4 Ambient1 Temperature and Humidity Limits

| Conditions | Limits |
| --- | --- |
| Temperature • Operating (up to 1829 m) • Short-term2 • Short-term with fan failure | 5°C to 40°C (41°F to 104°F) -5°C to 50°C (23°F to 122°F) -5°C to 40°C (23°F to 104°F) |
| Rate of temperature change | 30°C/hr (54°F/hr) |
| Relative Humidity • Operating • Short-term2 | 5% to 85% 5% to 90%, but not to exceed 0.024 kg water/kg of dry air |

Notes:

- Ambient refers to conditions at a location 1.5 m (59 in) above the floor and 400 mm (15.8 in) in front of the equipment. Frame-level products are tested to 50°C. Shelf-level products are tested to 55°C. Refer to Section 5.1, “Temperature, Humidity, and Altitude Test Methods,” for details of test conditions.

- Short-term refers to a period of not more than 96 consecutive hours and a total of not more than 15 days in 1 year. (This refers to a total of 360 hours in any given year, but no more than 15 occurrences during that 1-year period.)

Figure 4-1 Ambient Temperature and Humidity Limits

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R4-6 [72].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-5: Operating Temperature and Humidity Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Altitude (4.1.3)

### Criteria:

R4-7 [74]	All equipment shall be functional when installed at elevations between 61 m (200 ft) below sea level and 1829 m (6000 ft) above sea level at aisle-ambient temperatures of 40°C.

R4-8 [136]	All equipment shall be functional when installed at elevations between 1829 m (6000 ft) and 3960 m (13,000 ft) above sea level, at aisle-ambient temperatures of 30°C.

At elevations greater than 1829 m above sea level, the cooling capacity of ambient air is reduced due to its reduced density. It may be necessary to work with the purchaser to provide adequate cooling.

R4-9 [75]	The manufacturer shall provide special requirements for installations above 1829 m (6000 ft) in the product documentation, if needed.

O4-10 [137]	All equipment should be functional when installed at elevations between 61 m (200 ft) below sea level and 18290 m

(6000 ft) above sea level at aisle-ambient temperatures of 50°C.

O4-11 [76]	All equipment should be functional when installed at elevations between 1829 m (6000 ft) and 3960 m (13,000 ft) above sea level, at aisle-ambient temperatures of 40°C.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-7 [74], R4-8 [136], R4-9 [75], and Objectives O4-10 [137] and O4-11 [76].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-6: Altitude Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Temperature Margin Evaluation (4.1.4)

### Criteria:

R4-12 [153] 	Equipment response to temperatures up to 10°C above the short-term high temperature extreme of Table 4-4, “Ambient1 Temperature and Humidity Limits,” shall be determined. Report the threshold temperature for deterioration of functional performance and/or equipment shutdown.

Table 4-4 Ambient1 Temperature and Humidity Limits

| Conditions | Limits |
| --- | --- |
| Temperature • Operating (up to 1800 m) • Short-term2 • Short-term with fan failure | 5°C to 40°C (41°F to 104°F) -5°C to 50°C (23°F to 122°F) -5°C to 40°C (23°F to 104°F) |
| Rate of temperature change | 30°C/hr (54°F/hr) |
| Relative Humidity • Operating • Short-term2 | 5% to 85% 5% to 90%, but not to exceed 0.024 kg water/kg of dry air |

Notes:

- Ambient refers to conditions at a location 1.5 m (59 in) above the floor and 400 mm (15.8 in) in front of the equipment. Frame-level products are tested to 50°C. Shelf-level products are tested to 55°C. Refer to Section 5.1, “Temperature, Humidity, and Altitude Test Methods,” for details of test conditions.

- Short-term refers to a period of not more than 96 consecutive hours and a total of not more than 15 days in 1 year. (This refers to a total of 360 hours in any given year, but no more than 15 occurrences during that 1-year period.)

Figure 4-1 Ambient Temperature and Humidity Limits

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R4-12 [153].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-7: Temperature Margin Evaluation Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Equipment Fan-Performance Criteria (4.1.5.1)

### Criteria:

R4-13 [154] 	Equipment cooled by forced convection shall not sustain damage or deterioration of functional performance when operated with any single fan failure at a 40°C aisle ambient for a short-term of up to 96 hours per Table 4-4, “Ambient1 Temperature and Humidity Limits.”

R4-14 [155] 	Equipment cooled by forced convection shall have provisions for remote alarm notification of a fan failure.

O4-15 [156] 	Equipment cooled by forced convection should be designed and constructed such that any fan or cooling unit replacement can be performed with no service interruption.

R4-16 [157] 	The replacement procedure for fans and cooling units shall be included in the product documentation.

R4-17 [158] 	When a fan or cooling unit replacement requires service interruption, the estimated time of replacement by a skilled technician shall be reported.

Table 4-4 Ambient1 Temperature and Humidity Limits

| Conditions | Limits |
| --- | --- |
| Temperature • Operating (up to 1800 m) • Short-term2 • Short-term with fan failure | 5°C to 40°C (41°F to 104°F) -5°C to 50°C (23°F to 122°F) -5°C to 40°C (23°F to 104°F) |
| Rate of temperature change | 30°C/hr (54°F/hr) |
| Relative Humidity • Operating • Short-term2 | 5% to 85% 5% to 90%, but not to exceed 0.024 kg water/kg of dry air |

Notes:

- Ambient refers to conditions at a location 1.5 m (59 in) above the floor and 400 mm (15.8 in) in front of the equipment. Frame-level products are tested to 50°C. Shelf-level products are tested to 55°C. Refer to Section 5.1, “Temperature, Humidity, and Altitude Test Methods,” for details of test conditions.

- Short-term refers to a period of not more than 96 consecutive hours and a total of not more than 15 days in 1 year. (This refers to a total of 360 hours in any given year, but no more than 15 occurrences during that 1-year period.)

Figure 4-1 Ambient Temperature and Humidity Limits

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R4-13 [154], R4-14 [155], R4-16 [157], R4-17 [158] and Objective O4-15 [156].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-8: Equipment Fan Performance Criteria Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Equipment Fan-Filter Criteria (4.1.5.2)

### Criteria:

R4-18 [138]	All fan-cooled equipment shall be equipped with filters. Fan filters shall be replaceable with equipment operating. Fans used to cool the outside of sealed equipment cabinets need not be fitted with particulate filters.

R4-19 [139]	All equipment fan filters used in equipment occupying over 2U of vertical rack space (90 mm or 3.5 in) shall have either a:

- Minimum dust arrestance of 80%, per ASHRAE Standard 52.1, Gravimetric and Dust-Spot Procedures for Testing Air Cleaning Devices Used in General Ventilation for Removing Particulate Matter, or

- Minimum Efficiency Rating Value (MERV) of 4, per ASHRAE Standard 52.2, Method of Testing General Ventilation Air Cleaning Devices for Removal Efficiency by Particle Size.

R4-20 [176] 	All equipment fan filters used in equipment occupying 2U of vertical rack space (90 mm or 3.5 in) or less shall have either a:

- Minimum dust arrestance of 65%, per ASHRAE Standard 52.1, Gravimetric and Dust-Spot Procedures for Testing Air Cleaning Devices Used in General Ventilation for Removing Particulate Matter, or

- Minimum Efficiency Rating Value (MERV) of 2, per ASHRAE Standard 52.2, Method of Testing General Ventilation Air Cleaning Devices for Removal Efficiency by Particle Size.

R4--21 [140]	Fan filters shall have a minimum fire rating of Class 2 per UL 900-2004, Standard for Air Filter Units, plus revisions, and be marked “UL Classified.”.

R4-22 [141]	Construction and system fit of equipment fan filters shall prevent any air bypass. Inadvertent leakage that may result from mechanical fits or tolerances, (examples may include spaces between circuit pack face plates, connector or cable matrices, chassis screw or mounting holes, etc.), is not considered bypass.

R4-23 [142]	Equipment shall have provision for fan-filter replacement without particulate contaminants from the filter being introduced into equipment. If filters can be changed with fans operating, filter replacement methods that minimize touching the media and/or dislodging capture particulates shall be specified. Filter designs with rigid frames that are withdrawn from the airflow for removal satisfy the intent of this requirement.

R4-24 [143]	The equipment manufacturer shall provide a method for determining equipment fan filter replacement schedules.

O4-25 [144]	If possible, active alarming should be provided to indicate the need for fan filter replacement.

R4-26 [145]	Equipment fan filters shall be single use and not the types that require cleaning.

O4-27 [194]	It is an objective that equipment fan filters utilize recyclable materials..

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with R4-18 [138], R4-19 [139], R4-20 [176], R4-21 [140], R4-22 [141], R4-23 [142] R4-24 [143], R4-26 [145], and Objectives O4-25 [144], O4-27 [194].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-9: Equipment Fan Filter Criteria Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Heat Dissipation and Energy Efficiency (4.1.6)

### Criteria:

R4-28 [77]	The maximum rate of heat release and method of cooling (e.g., natural convection, forced-air fans) shall be documented for all equipment.

- For circuit packs, document the rate of heat release in Watts (W).

- For floor mounted equipment, document the heat release in W/m2 and W/ft2 of floor area.

- For equipment shelves, document the heat release in W/m2 per meter and W/ft2 per foot of frame vertical height used.

O4-29 [78] 	Equipment rate of heat dissipation should not exceed the values presented in Table 4-5. Heat dissipation greater than these objectives must be clearly identified in product documentation along with a note indicating that special equipment room cooling may be required. The heat dissipation objectives for an individual frame are based upon overall system heat dissipation that does not exceed the system values Table 4-5 provides.

Table 4-5. Equipment Area Heat Release Objective

| Individual Frame |  |
| --- | --- |
| Natural convection Forced-air fans | 1450 W/m2 (134.7 W/ft2) 1950 W/m2 (181.2 W/ft2) |
| Multi-Frame |  |
| Entire System Any 6.1-m by 6.1-m (20-ft by 20-ft) square area within a larger system | 860 W/m2 (79.9 W/ft2)* 1075 W/m2 (99.9 W/ft2)* |
| Shelf |  |
| Natural Convection Forced-air fans | 740 W/m2 per meter (20.9 W/ft2/ft) of vertical frame space the equipment uses. 995W/m2 per meter (27.9 W/ft2/ft) of vertical frame space the equipment uses. |

* Systems totally comprised of forced-air cooled equipment may increase these levels to 1075 W/m2 (99.9 W/ft2) and 1290 W/m2 (119.8 W/ft2).

O4-30 [195] 	Equipment intended for CO deployment should be compatible with dc power plants per ATIS-0600315.2007.

R4-31 [196] 	Equipment shall be tested to the applicable ATIS-0600015.2009, Energy Efficiency for Telecommunication Equipment: Methodology for Measurements and Reporting – General Requirements standard, or other specification identified by the service provider. The results shall be provided to the service provider.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-28 [77], R4-31 [196], and Objectives O4-29 [78], O4-30 [195].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-10: Heat Dissipation Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Surface Temperature (4.1.7)

### Criteria:

O4-32 [79] 	It is an objective that equipment surfaces that face aisles or surfaces where normal maintenance functions are anticipated shall not exceed 48°C (118°F) when the equipment is operating in a room with an ambient air temperature of 23°C (73°F). Passive equipment, wherein no heat is generated, are exempt from testing.

R4-33 [159] 	It is a requirement that equipment surfaces that face aisles or surfaces where normal maintenance functions are anticipated shall be in conformance to the temperature limits established in Table 4-6, “Temperature Limits of Touchable Surfaces,” when the equipment is operating in a room with an ambient air temperature of 23°C (73°F). Passive equipment, wherein no heat is generated, is exempt from testing.

Table 4-6 Temperature Limits of Touchable Surfaces

| Materials | Permitted Temperature (°C) as a Function of Exposure Times |  |
| --- | --- | --- |
|  | Unintentional Contact or Parts Held for Short Periods in Normal Use1 | Prolonged Use2 |
| Metals3 | 55 | 48 |
| Nonmetals | 70 | 48 |

Notes:

- Parts held in normal use are expected to be held up to 10 seconds. Examples may include extractor tabs, handles, knobs, and grips. Examples may also include surfaces handled during maintenance, repair, or upgrade.

- Prolonged use is anywhere between 10 seconds and 10 minutes. Examples may include surfaces handled during more extensive maintenance and repair procedures.

- Metals may be coated, uncoated, plated and/or have a conversion coating. Conversion coatings are assumed to be thermally conductive.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O4-32 [79], Requirement R4-33 [159].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-11: Surface Temperature Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Equipment Airflow (4.1.8)

### Criteria:

R4-34 [160] 	Air-cooled equipment shall utilize only a rear-aisle exhaust (EC Class X-R1, X-R2, X-R3, or a combination of these).

NOTE: Where approved by exception, top exhaust (EC Class X-T) airflow equipment may be deployed in support of specialized airflow requirements.

O4-35 [161] 	Air-cooled equipment shall utilize a front-aisle air inlet (EC Class F1-X, F2-X, F3-X, or a combination of these).

O4-36 [197] 	Air-cooled equipment with other than front-aisle to rear-aisle airflow should be fitted with manufacturer provided air baffles/deflectors that efficiently re-route the air to provide front-aisle to rear-aisle airflow.

R4-37 [198] 	Equipment requiring air baffles/deflectors for airflow compliance shall be tested by the manufacturer for compliance to GR-63-CORE with such hardware in place.

R4-38 [199] 	Air-cooled equipment with other than front-aisle air inlet shall not sustain any damage or deterioration of functional performance during its operating life when operated at elevated air-inlet temperatures per the test methods of Section 5.1, “Temperature, Humidity, and Altitude Test Methods.”.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-34 [ 160], R4-37 [198], R4-38 [199] and Objectives O4-35 [161] and O4-36 [197].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 20-12: Equipment Airflow Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

<<Insert tables with detailed description of equipment pack fill>>