TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

Part 21

fire resistance

Section 4.2, GR-63-CORE

Telcordia Technologies GR-63, Issue 4, April 2012

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Page

Test Results Summary	3

Overview	5

Frame-Level Fire-Resistance Criteria (4.2.2.1)	6

Shelf-Level Fire-Resistance Criteria (4.2.2.2)	8

Smoke and Self-Extinguishment Criteria (4.2.2.3)	10

Material/Components Fire-Resistance Criteria (4.2.3.1)	11

Wire and Cable Between Frames (4.2.3.2)	13

Optical Fiber Cable Trays and Raceways (4.2.3.3)	15

Igntability Requirements for Ancillary Materials (4.2.3.4)	16

Appendix A	17

- LIST OF TABLES

Page

Table 21-1: Fire Resistance Summary of Test Results	3

Table 21-2: Frame-Level Fire Resistance Detailed List of Test Equipment	7

Table 21-3: Shelf-Level Fire Resistance Detailed List of Test Equipment	9

Table 21-4: Smoke and Self-Extinguishment Criteria Detailed List of Test Equipment	10

Table 21-5: Material/ Components Fire Resistance Detailed List of Test Equipment	12

Table 21-6: Wire and Cable Between Frames Detailed List of Test Equipment	14

Table 21-7: Optical Fiber Cable Trays and Raceways Detailed List of Test Equipment	15

- LIST OF FIGURES

Page

Error! No table of figures entries found.

## Test Results Summary

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-63-CORE.

- Section Name column gives the Section name from GR-63-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-63-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, Non-compliant, etc.).

- Compliant: The Equipment Under Test met the requirements of the corresponding criteria.

- Non-compliant: The Equipment Under Test did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to Equipment Under Test {Explanation Required}

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- Page column gives the page number, in this report, for the corresponding criteria.

Table 21-1: Fire Resistance Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Section | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 4.2 | Fire Resistance | - |  |  |  |
| 4.2.2 | Equipment Assembly Fire Tests | - |  |  |  |
| 4.2.2.1 | Frame-Level Fire-Resistance Criteria | - |  |  |  |
|  | A. Fire spread Criteria | R4-39 [81] |  |  | 6 |
|  |  | R4-40 [162] |  |  | 6 |
|  | B. Fire Propagation Hazard Characterization | R4-41 [82] |  |  | 6 |
|  |  | O4-42 [83] |  |  | 6 |
|  |  | O4-43 [84] |  |  | 6 |
|  |  | O4-44 [200] |  |  | 6 |
| 4.2.2.2 | Shelf-Level Fire-Resistance Criteria | - |  |  |  |
|  | A. Fire spread Criteria | R4-45 [86] |  |  | 8 |
|  |  | R4-46 [163] |  |  | 8 |
|  | B. Fire Propagation Hazard Characterization | R4-47 [87] |  |  | 8 |
|  |  | O4-48 [88] |  |  | 8 |
|  |  | O4-49 [89] |  |  | 8 |
|  |  | O4-50 [201] |  |  | 8 |
| 4.2.2.3 | Smoke and Self-Extinguishment Criteria | O4-51 [164] |  |  | 10 |
|  |  | O4-52 [165] |  |  | 10 |
|  |  | R4-53 [166] |  |  | 10 |
|  |  | O4-54 [167] |  |  | 10 |
|  |  | R4-55 [168] |  |  | 10 |
|  |  | O4-56 [202] |  |  | 10 |
| 4.2.3 | Use of Fire-Resistant Materials, Components, Wiring, and Cable | - |  |  |  |
| 4.2.3.1 | Material/Comp. Fire-Resistance Criteria | R4-57 [90] |  |  | 12 |
|  |  | R4-58 [203] |  |  | 12 |
|  | A. Mechanical Elements | R4-59 [91] |  |  | 12 |
|  |  | R4-60 [92] |  |  | 12 |
|  |  | R4-61 [93] |  |  | 12 |
|  |  | R4-62 [95] |  |  | 12 |
|  |  | R4-63 [96] |  |  | 12 |
|  |  | R4-64 [204] |  |  | 12 |
|  | B. Electronic Components | R4-65 [97] |  |  | 12 |
|  | C. Interconnect Wire | R4-66 [98] |  |  | 12 |
|  | D. Interconnecting Optical Fiber | R4-67 [205] |  |  | 12 |
| 4.2.3.2 | Wire and Cable Between Frames - Wire and Cable in Duct or Plenum Spaces B. Wire and Cable in Riser Shafts C. Wire and Cable in Other Spaces D. Limited Smoke Wire and Cable E. AC-Powered Wiring and Fittings | R4-68 [100] |  |  | 13 |
|  |  | R4-69 [101] |  |  | 13 |
|  |  | R4-70 [102] |  |  | 13 |
|  |  | R4-71 [103] |  |  | 13 |
|  |  | O4-72 [104] |  |  | 13 |
|  |  | R4-73 [105] |  |  | 13 |
| 4.2.3.3 | Optical Fiber Cable Trays and Raceways | R4-74 [169] |  |  | 15 |
|  |  | R4-75 [170] |  |  | 15 |
|  |  | R4-76 [171] |  |  | 15 |
| 4.2.3.4 | Ignitability Requirements for Ancillary Materials | R4-77 [172] |  |  | 15 |
|  |  | R4-78 [173] |  |  | 15 |
|  |  | R4-79 [174] |  |  | 15 |

## Overview

### Project Objective

Testing was performed to determine if the <Product Name> met the requirements for Section 4.2, Fire Resistance, of GR-63-CORE, Issue 4, April 2012.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

## Frame-Level Fire-Resistance Criteria (4.2.2.1)

### Criteria:

R4-39 [81] 	When tested following the procedures of ATIS-0600319.2008 and the modifications of GR-63-CORE Section 5.2, fire shall not spread beyond the confines of the equipment assembly being tested. In accordance with ATIS-0600319.2008, the fire shall be judged to have spread beyond the equipment under test if any of the following occur:

- Sustain ignition to an adjacent equipment enclosure or printed circuit board material of an adjacent equipment shelf

- Ignition of the Frame Level Ignition Indicator Module (FLIIM).

R4-40 [162] 	When tested following the procedures of ATIS-0600319.2008 and the modifications of GR-63-CORE Section 5.2, the equipment shall not demonstrate excessive surface burning or external flaming. The equipment shall be judged to have excessive surface burning or external flaming if the following occurs:

- Flames (other than flames from the methane line burner) in excess of 50 mm in any dimension and extending beyond the top or bottom of the equipment under test for 30 seconds or more, after 170 seconds from the start of the line burner profile.

- Flames (other than flames from the methane line burner) in excess of 50 mm in any dimension extending beyond any confines of the front, rear or sides of the equipment under test continuously for 30 seconds or more.

R4-41 [82] 	The fire propagation hazard shall be characterized by measuring and recording the rate of heat release of the equipment fire as tested by the methods of Section 5.2, “Fire Test Methods.”

O4-42 [83] 	The peak rate of heat release measured should not exceed 150 kW at any time during the test.

O4-43 [84] 	The average rate of heat release should not exceed 100 kW over any 30-minute period during the test.

O4-44 [200] 	Frame-level equipment tested and conforming to the Fire-Spread and Fire-Propagation Hazard Characterization criteria as a result of fans/blowers preventing line-burner operation, should demonstrate conformance to the Fire-Spread and Fire-Propagation Hazard Characterization criteria when product fans are not powered.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <TCG Certified ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-39 [81], R4-40 [162] and R4-41 [82], and Objectives O4-42 [83], O4-43 [84] and O4-44 [200].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 21-2: Frame-Level Fire Resistance Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Shelf-Level Fire-Resistance Criteria (4.2.2.2)

### Criteria:

R4-45 [86] 	When tested following the procedures of ATIS-0600319.2008 and the modifications of GR-63-CORE Section 5.2, fire shall not spread beyond the confines of the equipment assembly being tested. In accordance with ATIS-0600319.2008, the fire shall be judged to have spread beyond the equipment under test if the following occurs:

- Ignition of the Shelf Level Ignition Indicator Module (SLIIM).

R4-46 [163] 	When tested following the procedures of ATIS-0600319.2008 and the modifications of GR-63-CORE Section 5.2, the equipment shall not demonstrate excessive surface burning or external flaming. The equipment shall be judged to have excessive surface burning or external flaming if any of the following occur:

- Flames (other than flames from the methane line burner) in excess of 50 mm in any dimension and extending beyond the top or bottom of the equipment under test for 30 seconds or more, after 170 seconds from the start of the line burner profile.

- Flames (other than flames from the methane line burner) in excess of 50 mm in any dimension extending beyond any confines of the front, rear or sides of the equipment under test continuously for 30 seconds or more.

R4-47 [87] 	The fire propagation hazard shall be characterized by measuring and recording the rate of heat release of the equipment fire, as tested by the methods of Section 5.2, “Fire Test Methods.”

O4-48 [88] 	The peak rate of heat release measured should not exceed 50 kW at any time during the test.

O4-49 [89] 	The average rate of heat release should not exceed 35 kW during any 15-minute period during the test.

O4-50 [201] 	Shelf-level equipment tested and conforming to the Fire-Spread and Fire-Propagation Hazard Characterization criteria as a result of fans/blowers preventing line-burner operation, should demonstrate conformance to the Fire-Spread and Fire-Propagation Hazard Characterization criteria when product fans are not powered.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-45 [86], R4-46 [163], R4-47 [87], and Objectives O4-48 [88], O4-49 [89] and O4-50 [201].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 21-3: Shelf-Level Fire Resistance Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Smoke and Self-Extinguishment Criteria (4.2.2.3)

### Criteria:

O4-51 [164] 	At 4 minutes and 30 seconds into the test, after the conclusion of the methane ignition line burn, the components in the equipment assembly should show evidence of beginning to self-extinguish.

O4-52 [165] 	At 10 minutes into the test, there should be a significant flame reduction and a reduction in the visible smoke from the equipment assembly as determined by visual observations and supported by the video record and analytic smoke measurements.

R4-53 [166] 	At 15 minutes into the test, flames shall be extinguished.

O4-54 [167] 	At 15 minutes into the test, there should be no more than minimal wisps of smoke from the equipment assembly as determined by visible observations and supported by the video record and analytic smoke measurements.

R4-55 [168] 	At 20 minutes into the test, there shall be no visible smoke from the equipment assembly as determined by visible observations and supported by the video record and analytic smoke measurements.

O4-56 [202] 	Equipment tested and conforming to the Fire-Spread and Fire-Propagation Hazard Characterization criteria as a result of fans/blowers preventing line-burner operation, should demonstrate conformance to the Fire-Spread and Fire-Propagation Hazard Characterization criteria when product fans are not powered.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-53 [166] and R4-55 [168], and Objectives O4-51 [164], O4-52 [165], O4-54 [167] and O4-56 [202].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 21-4: Smoke and Self-Extinguishment Criteria Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Material/Components Fire-Resistance Criteria (4.2.3.1)

### Criteria:

R4-57 [90] 	All materials, components, and interconnect wire and cable used within equipment assemblies shall meet the requirements of Section 4.1 of ANSI T1.307- 2007, Fire-Resistance Criteria - Ignitability Requirements for Equipment Assemblies, Ancillary Non-Metallic Apparatus, and Fire Spread Requirements for Wire and Cable, Section 4.1.

Components contained within a small metal fire enclosure do not present risk of self-ignition due to lack of oxygen and lack of potential for fire spread. This requirement, R4-57 [ 90], does not apply to materials and components within an enclosure of 0.005 m3 (305 in3) or less, consisting totally of metal and having no intentional ventilation openings. Interfaces entering or leaving a fire enclosure are not considered intentional ventilation openings if they pass from the enclosure with minimal clearance.

R4-58 [203] 	Components and materials exposed or outside of a fire enclosure shall conform to R4-57 [90].

A technical design assessment shall be performed by the testing authority to determine if an assembly meets the defined criteria as a qualified fire enclosure. Photographs and documentation of engineering assessment to justify this interpretation should be included in the NEBS test report..

R4-59 [91] 	Mechanical components (examples include circuit boards, backplanes, connectors, and plastic covers and handles) shall be either:

- Rated SC 0, SC 1, SC-TC 0 or SC-TC 1, or

- Formed of materials that, in the minimum thickness as used in the component, are rated UL 94 V-0 as determined by ANSI/UL 94-1996, Test for flammability of plastic materials for parts in devices and appliances, or

- Formed of materials that, in the minimum thickness as used in the component, are rated UL 94 V-1 and have an oxygen index of 28% or greater as determined by ASTM D2863-00, Standard Test Method for Measuring the Minimum Oxygen Concentration to Support Candle-Like Combustion of Plastics (Oxygen Index), or

- Conforming to the needle flame test of ANSI T1.307-2003 (Section 5.1), or

- Conforming to the in-situ needle flame test of ANSI T1.307-2003 (Section 5.2), or

- Conforming to the Telcordia needle flame test of Section 5.2.3.1 of this GR, or

- Conforming to the Telcordia in-situ needle flame test of Section 5.2.3.2 of this GR.

Discrete structural components with overall dimensions of 6.3 mm (1/4 inch) x 6.3 mm (1/4 inch) x 6.3 mm (1/4 inch) or less or constituting a fuel load of 1 gram (0.035 oz.) or less are exempt from the requirements of R [91]. If such components are grouped in close proximity and their total mass exceeds 1 gram (0.035 oz.) they shall comply with R [92].

R4-60 [92] 	Small discrete structural components, grouped in close proximity, as described in the second paragraph of R4-43 [91], shall be tested to the needle flame test, as described in ANSI T1.307-2003 (Section 5.2), or the Telcordia needle flame test of Section 5.2.3. The ignition of one component by the test flame shall not ignite any adjacent component.

R4-61 [93] 	Foamed polymers shall meet the HF-1 requirements of ANSI/UL 94-1996.

NOTE: Foamed polymer air filter assemblies must also meet the firespread requirements of Section 4.1.5.2, “Equipment Fan-Filter Criteria.”

R4-62 [95]	 Insulating tapes shall meet the flammability requirements of UL 510-2005,Insulating Tape.

R4-63 [96] 	Sleeving and tubing flammability shall meet the VW-1 requirements of ANSI/UL 1441-1995, Coated Electrical Sleeving.

R4-64 [204] 	The flammability of miscellaneous sleeving and tubing used for mechanical support and protection of optical fibers shall meet R4-59 [91] or R4-60 [92], or the VW-1 requirements when tested to the flammability test methods of ANSI/UL 1441-2005, Coated Electrical Sleeving.

R4-65 [97] 	Discrete electronic components shall be either:

- Conforming to the needle flame test of ANSI T1.307-2007, Section 5.1, or

- Conforming to the in-situ needle flame test of ANSI T1.307-2007, Section 5.2,

Or

- Conforming to the Telcordia needle flame test of Section 5.2.4.1 of this GR, or

- Conforming to the Telcordia in-situ needle flame test of this GR, or

- Be rated SC 0, SC 1, SC-TC 0 or SC-TC 1, or

- Formed of materials that, in the minimum thickness as used in the component, are rated UL 94 V-0 as determined by ANSI/UL 94-1996, or

- Formed of materials that, in the minimum thickness as used in the component, are rated UL 94 V-1 and have an oxygen index of 28% or greater as determined by ASTM D2863-10.

R4-66 [98] 	Interconnect wire shall satisfy the VW-1 requirements contained in ANSI/UL 1581-2001, Reference standard for electrical wires, cables, and flexible cords.

R4-67 [205] 	Interconnecting optical fibers shall demonstrate adequate resistance. This shall be accomplished by conformance to R4-59 [91], R4-60 [92], R4-69 [101], R4-70 [102], or R4-71 [103]. Method of conformance shall be documented in the test report.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with R4-57 [90], R4-58 [203], R4-59 [91], R4-60 [92], R4-61 [93], R4-62 [95], R4-63 [96], R4-64 [204], R4-65 [97], R4-66 [98], and R4-67 [205].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 21-5: Material/ Components Fire Resistance Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Wire and Cable Between Frames (4.2.3.2)

### Criteria:

R4-68 [100] 	This requirement has been deleted, and. is incorporated into other Section 4 requirements.

R4-69 [101] 	Communications wiring used in air-handling ducts and plenums shall have a maximum flame spread of 1.5 m, a maximum peak optical smoke density smoke value of 0.5, and a maximum average optical density value of 0.15 when tested in accordance with ANSI/NFPA 262-2011, Standard Method of Test for Flame Travel and Smoke of Wires and Cables for Use in Air Handling Spaces. Power wire and cable used in air handling ducts and plenums shall comply with Article 300-22 of ANSI/NFPA 70-2011.

Cable types rated CMP, CL2P, CL3P, OFNP, MPP, FPLP, or CATVP conform to this requirement

R4-70 [102] 	Wire and cable used in riser shafts shall satisfy the flammability requirements of ANSI/UL 1666-2007, Test for Flame Propagation Height of Electrical and Optical-Fiber Cables Installed Vertically in Shafts.

Cable types rated CMR, CL2R, OFNR, MPR, FPLR, or CATVR, as well as those conforming to R4-69 [101], conform to this R4-70 [102] requirement.

R4-71 [103] 	Communication and power wire and cables running either horizontally or vertically in other spaces including dedicated cable pathways or cross-connect equipment, shall meet one of the following requirements:

- ANSI/UL 1685 -2007, Standard for Vertical-tray fire-propagation and smoke-release test for electrical and optical-fiber cable, or

- CAN/CS-C22.2 No. 0.3-09, Test methods for electrical wires and cables, or

- ANSI/IEEE 1202-2006, Standard for Flame-Propagation testing of wire and cables.

Cable types rated CM, CL2, CL3, OFN, OFC, MP, FPL or CATV, as well as those conforming to R4-69 [101] or R4-70 [102], conform to thisR4-71 [103] requirement.

O4-72 [104] 	Communication, power, and riser wire and cable should satisfy the requirements for smoke emission levels of ANSI/UL 1685-2007.

R4-73 [105] 	All ac-powered wiring and fittings in equipment shall meet the flammability requirements referenced by the National Electrical Code (NEC), i.e., NFPA 70, for their specific use in the equipment.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-68 [100], R4-69 [101], R4-70 [102], R4-71 [103], and R4-73 [105] and Objective O4-72 [104].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 21-6: Wire and Cable Between Frames Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Optical Fiber Cable Trays and Raceways (4.2.3.3)

### Criteria:

R4-74 [169] 	Optical fiber cable tray/raceway used in air handling ducts and plenums shall have a maximum flame spread of 5 ft (1.52 m), a maximum peak optical smoke density smoke value of 0.5, and a maximum average optical density value of 0.15 when tested in accordance with the Test for Flame Propagation and Smoke Density Values (Plenum) of ANSI/UL 2024-2011, Standard for Signaling, Optical Fiber and Communications Raceways and Cable Routing Assemblies.

R4-75 [170] 	Optical fiber cable tray/raceway used in riser shafts shall satisfy the flammability requirements of the Test for Flame Propagation (Riser) of ANSI/UL 2024-2011.

R4-76 [171] 	Optical fiber cable tray/raceway used in spaces other than duct, plenum or riser spaces shall comply with the Vertical Tray Flame Test (General) of ANSI/UL 2024-2011.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-74 [169], R4-75 [170] and R4-76 [171].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 21-7: Optical Fiber Cable Trays and Raceways Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Igntability Requirements for Ancillary Materials (4.2.3.4)

### Criteria:

R4-77 [172] 	Products having an exposed surface area < 1 ft2 (0.09 m2) shall be formed from materials having a fire-resistance characteristic equivalent to or better than UL 94 V-0 as determined by ANSI/UL 94-1996.

R4-78 [173] 	Products having an exposed surface area > 1 ft2 (0.09 m2) to 10 ft2 (0.93 m2) shall be formed from materials having a fire-resistance characteristic equivalent to or better than UL-94 5VA as determined by ANSI/UL 94-1996.

R4-79 [174]	Products having an exposed surface area > 10 ft2 (0.93 m2) shall be formed from materials having a fire-resistance characteristic equivalent to or better than UL-94 5VA as determined by ANSI/UL 94-1996, and shall have a flame-spread rating of <200.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R4-77 [172], R4-78 [173] and R4-79 [174].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 21-8: Ignitability Requirements for Ancillary Materials Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

<<Insert tables with detailed description of equipment pack fill>>