TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

Part 23

Earthquake, office vibration, and transportation vibration

Section 4.4, GR-63-CORE

Telcordia Technologies GR-63, Issue 4, April 2012

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Page

Test Results Summary	3

Overview	5

Earthquake Environment and Criteria (4.4.1)	6

Framework and Anchor Criteria (4.4.2)	8

Wall-Mounted Equipment Anchor Criterion (4.4.3)	10

Office Vibration Environment and Criteria (4.4.4)	11

Transportation Vibration Criteria (4.4.4)	12

Appendix A	13

- LIST OF TABLES

Page

Table 23-1: Earthquake, Office Vibration, and Transportation Vibration Summary of Test Results	3

Table 23-2: Earthquake Environment Detailed List of Test Equipment	7

Table 23-3: Framework and Anchor Detailed List of Test Equipment	9

Table 23-4: Wall-Mounted Equipment Anchor Detailed List of Test Equipment	10

Table 23-5: Office Vibration Environment and Criteria Detailed List of Test Equipment	11

Table 23-6: Transportation Vibration Detailed List of Test Equipment	12

- LIST OF FIGURES

Page

Error! No table of figures entries found.

## Test Results Summary

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-63-CORE.

- Section Name column gives the Section name from GR-63-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-63-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, Non-compliant, etc.).

- Compliant: The Equipment Under Test met the requirements of the corresponding criteria.

- Non-compliant: The Equipment Under Test did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to Equipment Under Test {Explanation Required}

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- Page column gives the page number, in this report, for the corresponding criteria.

Table 23-1: Earthquake, Office Vibration, and Transportation Vibration Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Comments | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 4.4 | Earthquake, Office Vibration, and Transportation Vibration | - | - |  | - |
| 4.4.1 | Earthquake Environment and Criteria | - | - |  | - |
| 4.4.1.2 | Physical Performance Criteria | R4-83 [110] |  |  | 6 |
|  |  | R4-84 [111] |  |  | 6 |
|  |  | R4-85 [112] |  |  | 6 |
|  |  | O4-86 [113] |  |  | 6 |
| 4.4.1.3 | Functional Performance | R4-87 [114] |  |  | 6 |
|  |  | O4-88 [115] |  |  | 6 |
| 4.4.2 | Framework and Anchor Criteria | O4-89 [116] |  |  | 8 |
|  |  | R4-90 [117] |  |  | 8 |
|  |  | O4-91 [118] |  |  | 8 |
|  |  | R4-92 [119] |  |  | 8 |
|  |  | O4-93 [120] |  |  | 8 |
|  |  | O4-94 [121] |  |  | 8 |
| 4.4.3 | Wall-Mounted Equipment Anchor Criterion | R4-95 [175] |  |  | 10 |
| 4.4.4 | Office Vibration Environment and Criteria Physical Performance Criteria Functional Performance Criteria | - | - | - |  |
|  |  | R4-96 [122] |  |  | 11 |
|  |  | R4-97 [123] |  |  | 11 |
| 4.4.4 | Transportation Vibration Criteria Transportation Environment | - | - |  | - |
|  |  | R4-98 [124] |  |  | 12 |

## Overview

### Project Objective

Testing was performed to determine if the «ProductName» met the requirements for Section 4.4, Earthquake, Office Vibration, and Transportation Vibration, of Telcordia Technologies GR-63-CORE, Issue 3, March 2006.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

## Earthquake Environment and Criteria (4.4.1)

### Physical Performance Criteria (4.4.1.2)

### Criteria:

During this test, only the equipment shelf’s physical performance is considered. Permanent structural or mechanical damage of the framework or its fastening hardware would not constitute a failure, but may invalidate the test.

Permanent structural damage is defined as deformation of any load-bearing element of the equipment being tested, or any connection failure. Typical examples of permanent structural damage are bent or buckled uprights, deformed bases, cracks, and failed anchors or fastening hardware.

Mechanical damage is defined as any dislocation or separation of components. Examples of mechanical damage are disengaged cards and modules, and opened (ajar) doors, drawers, or covers.

R4-83 [110]	All equipment shall be constructed to sustain the waveform testing of Section 5.4.1 without permanent structural or mechanical damage.

R4-84 [111]	Frame-level equipment shall be constructed so that during the waveform testing of Section 5.4.1, the maximum single-amplitude deflection at the top of the framework, relative to the base, does not exceed 75 mm (3 in).

R4-85 [112]	Frame-level equipment shall have a natural mechanical frequency greater than 2.0 Hz as determined by the swept sine survey of Section 5.4.1.

O4-86 [113]	Frame-level equipment should have a natural mechanical frequency greater than 6.0 Hz as determined by the swept sine survey of Section 5.4.1.

### Functional Performance (4.4.1.3)

### Criteria:

The criterion for assessing functionality depends on the service provided by the equipment being tested. The criteria are determined by applying appropriate Telcordia generic requirements or, if none exist, by reviewing the supplier’s or purchaser’s own performance specifications.

R4-87 [114]	All equipment shall be constructed to meet applicable functionality requirements immediately before and after each axis of waveform testing of Section 5.4.1.  The equipment shall sustain operation without replacement of components, manual rebooting, or human intervention.

O4-88 [115]	All equipment should be constructed to meet applicable functionality requirements continuously during waveform testing of Section 5.4.1.  These functionality criteria shall demonstrate that the equipment has sustained operation without loss of service during the testing.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The «ProductName» is compliant/not compliant with Requirements R4-83 [110], R4-84 [111], R4-85 [112], R4-87 [114] and Objectives O4-86 [113], O4-88 [115].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 23-2: Earthquake Environment Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Framework and Anchor Criteria (4.4.2)

### Criteria:

The following criteria apply to all framework and concrete expansion anchors used in network facilities. They are intended to ensure minimum limits for structural performance in earthquake environments are met.

O4-89 [116]	Framework should be of welded construction.

R4-90 [117]	Framework shall be constructed for base mounting to the floor without auxiliary support or bracing from the building walls or ceilings.

O4-91 [118]	For framework used in earthquake risk zones, the static pull testing procedures of Section 5.4.1.4 should be followed, meeting these objectives:

- The maximum single amplitude deflection at the top of the framework should not exceed 75 mm (3 in).

- The top of the framework should return to its original position, within 6 mm (0.24 in) when the load is removed.

- The framework should sustain no permanent structural damage during static framework testing.

R4-92 [119]	Concrete expansion anchors used to base mount framework to the floor shall meet the following requirements:

- Maximum embedment depth of 90 mm (3.5 in)

- Maximum bolt diameter of 13 mm (0.5 in).

O4-93 [120]	Concrete expansion anchors used to base mount the framework to the floor should be suitable for earthquake (dynamic) applications, as specified by the manufacturer.

O4-94 [121]	Concrete expansion anchors should use steel construction to minimize creep.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The «ProductName» is compliant/ not compliant with Requirements R4-90 [117] and R4-92 [119] and Objectives O4-89 [116], O4-91 [118], O4-93 [120], and O4-94 [121].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 23-3: Framework and Anchor Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Wall-Mounted Equipment Anchor Criterion (4.4.3)

### Criteria:

R4-95 [175] 	Fastening systems used for wall-mounted equipment shall withstand a force of 3 times the weight of the equipment applied to the equipment in any direction.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with R4-95 [175].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 23-4: Wall-Mounted Equipment Anchor Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Office Vibration Environment and Criteria (4.4.4)

### Physical Performance Criteria (4.4.4.2)

### Criteria:

R4-96 [122]	All equipment shall be constructed to sustain the office vibration testing of Section 5.4.2, “Office Vibration Test Procedure,” without permanent structural or mechanical damage.

### Functional Performance Criteria (4.4.4.3)

### Criteria:

R4-97 [123]	All equipment shall be constructed to meet applicable functionality requirements continuously during each axis of the office vibration testing of Section 5.4.2, “Office Vibration Test Procedure.” The equipment shall sustain operation without replacement of components, manual rebooting, or human intervention.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with R4-96 [122], R4-97 [123].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 23-5: Office Vibration Environment and Criteria Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

## Transportation Vibration Criteria (4.4.4)

### Criteria:

R4-98 [124]	Equipment shall not sustain any physical damage or deteriorate in functional performance when subjected to vibration levels expected during transportation.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The «ProductName» is compliant/ not compliant with R4-98 [124].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

### Test Equipment Used

Table 23-6: Transportation Vibration Detailed List of Test Equipment

| Description | Serial Number | Manufacturer | Model | Cal. Date | Cal. Due |
| --- | --- | --- | --- | --- | --- |

<<Fill out the table of test equipment used for this test ONLY>>

<<Insert tables with detailed description of equipment pack fill>>