TCG NEBS COMPLIANCE TEST Report FOR:

<Name of Company>

<Company Address>

Product: <Product Name>

Part 18

Facility and Space Planning Requirements

Section 2, GR-63-CORE

Telcordia Technologies GR-63, Issue 4, April 2012

Date: <<date>>

Project: <Project #, if applicable>

Job: <Job #, if applicable>

Report: <Report #>

TABLE OF CONTENTS

Page

Test Results Summary	3

Overview	5

Equipment Frames and Lineup Conformity (2.1)	6

Floor Plans (2.2)	7

Vertical Space Allocation (2.3)	8

Equipment Frame Floor Loading (2.3.2)	9

Space Planning for Distributing Frames (DFs) (2.4)	10

Space Planning for Centralized DC Power Plant Equipment (2.5)	11

Overhead Cable Distribution (2.6.1.2)	12

Cable Distribution Under Raised Floor (2.6.1.3)	13

CDS Floor Load and Support (2.6.4)	14

CEF Spatial Requirements (2.8.1)	15

CEF Loading Requirements (2.8.2)	16

Quality of Light  (2.12.1.1)	17

Luminance Ratios (2.12.1.2)	18

Color of Light (2.12.1.3)	19

Appendix A	20

- LIST OF TABLES

Page

Table 18-1: Spatial Requirements Summary of Test Results	3

- LIST OF FIGURES

Page

Error! No table of figures entries found.

## Test Results Summary

<<Summarize the test results here, including hardware changes or changes in product configuration during the testing.  While this is a summary, it should contain most of the relevant details to the tests and the test results>>

### Column Heading Definitions for Summary of Test Results Table

The following Summary of Test Results table contains these columns of information:

- Section column gives the Section numbers from GR-63-CORE.

- Section Name column gives the Section name from GR-63-CORE.

- Criteria column gives the local number of the requirement (e.g., R3-1) from GR-63-CORE and the absolute number of the requirement (e.g., [2]).

- Results column gives the results of the evaluation (Compliant, Non-compliant, etc.).

- Compliant: The Equipment Under Test met the requirements of the corresponding criteria.

- Non-compliant: The Equipment Under Test did not meet the requirements of the corresponding criteria.

- NA: The criteria were Not Applicable to Equipment Under Test {Explanation Required}

- ENR: An Evaluation, to these criteria, was Not Requested by the customer.

- Page column gives the page number, in this report, for the corresponding criteria.

Table 18-1: Facility and Space Planning Requirements Summary of Test Results

| ##### Section | ##### Section Name | ##### Criteria | ##### Results #### Pass/ Fail/ NA | ##### Comments | ##### Page |
| --- | --- | --- | --- | --- | --- |
| 2. | - Facility and Space Planning Requirements | - | - |  | - |
| 2.1 | Equipment Frames and Lineup Conformity | R2-1 [178] |  |  | 6 |
|  |  | O2-2 [4] |  |  | 6 |
|  |  | O2-3 [7] |  |  | 6 |
|  |  | O2-4 [8] |  |  | 6 |
| 2.2 | Floor Plans | R2-5 [179] |  |  | 7 |
|  |  | O2-6 [9] |  |  | 7 |
|  |  | R2-7 [146] |  |  | 7 |
|  |  | R2-8 [147] |  |  | 7 |
|  |  | O2-9 [10] |  |  | 7 |
|  |  | O2-10 [11] |  |  | 7 |
| 2.3 | Vertical Space Allocation | O2-11 [13] |  |  | 8 |
| 2.3.2 | Equipment Frame Floor Loading | O2-12 [18] |  |  | 9 |
|  |  | R2-13 [19] |  |  | 9 |
| 2.4 | Space Planning for Distributing Frames (DFs) | O2-14 [22] |  |  | 10 |
|  |  | O2-15 [24] |  |  | 10 |
| 2.5 | Space Planning for Centralized DC Power plant Equipment | R2-16 [25] |  |  | 11 |
|  |  | O2-17 [27] |  |  | 11 |
|  |  | O2-18 [28] |  |  | 11 |
| 2.6 | Cable Distribution Systems (CDSs) | - | - |  |  |
| 2.6.1 | Cable Distribution Requirements | - | - |  |  |
| 2.6.1.2 | Overhead Cable Distribution | O2-19 [29] |  |  | 12 |
|  |  | O2-20 [30] |  |  | 12 |
|  |  | O2-21 [31] |  |  | 12 |
|  |  | O2-22 [32] |  |  | 12 |
|  |  | O2-23 [33] |  |  | 12 |
| 2.6.1.3 | Cable Distribution Under Raised Floor | R2-24 [34] |  |  | 13 |
|  |  | R2-25 [35] |  |  | 13 |
|  |  | O2-26 [36] |  |  | 13 |
| 2.6.4 | CDS Floor Load and Support | O2-27 [37] |  |  | 14 |
| 2.8.1 | CEF Spatial Requirements | O2-28 [39] |  |  | 15 |
| 2.8.2 | CEF Loading Requirements | O2-29 [40] |  |  | 16 |
|  |  | R2-30 [41] |  |  | 16 |
| 2.12 | Illumination of Equipment Spaces | - | - |  |  |
| 2.12.1 | Illumination Criteria for Central Office (CO) Lighting Systems | - | - |  |  |
| 2.12.1.1 | Quality of Light | R2-31 [129] |  |  | 17 |
|  |  | O2-32 [130] |  |  | 17 |
|  |  | R2-33 [131] |  |  | 17 |
| 2.12.1.2 | Luminance Ratios | O2-34 [134] |  |  | 18 |
| 2.12.1.3 | Color of Light | O2-35 [135] |  |  | 19 |

## Overview

### Project Objective

Testing was performed to determine if the <Product Name> met the requirements for Section 2, Facility and Space Planning Requirements, of GR-63-CORE, Issue 4, April 2012.

### Equipment Configuration and Test Conditions

<Specify number of samples tested>

<<Describe EUT Configuration using photographs, diagrams, words, or any combination thereof>>

<<Detailed pack-fill information should be entered in a table in Appendix A at the end of this section>>

### Equipment Operating Conditions

<<Place pictures and diagrams of EUT operational set-up>>

### Pass/ Fail Criteria

<<Provide pass/fail criteria for the test>>

## Equipment Frames and Lineup Conformity (2.1)

### Criteria:

R2-1 [178]	Floor plans shall arrange equipment frames side-to-side in lineups.

O2-2 [4]	Frames of only one depth should be used in a frame lineup.

O2-3 [7]	The fronts of the base of all frames should be aligned.

O2-4 [8]	In the lineup, side clearance of at least 2 mm (0.08 in) should be provided between adjacent frames.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R2-1 [178] and Objectives O2-2 [4], O2-3 [7], and O2-4 [8].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Floor Plans (2.2)

### Criteria:

R2-5 [179]	Equipment frames used in back-to-back lineup floor plans must be designed for front access only.

O2-6 [9]	Floor plans should provide a high degree of standardization while maintaining enough flexibility to permit natural growth from the initial to the ultimate equipment configuration.  For 305-mm (12-in) deep frames, the 6-lineup plan shown in Figure 2-1 should be used.

R2-7 [146] 	Minimum aisle spacing for the all equipment areas shall be nominal 760 mm (2 ft, 6 in) for the maintenance aisle and nominal 600 mm (2 ft) for the wiring aisle.

R2-8 [147] 	Minimum main aisle spacing for all equipment areas shall be nominal 1200 mm (4 ft) between groups of equipment lineups.

O2-9 [10]	Floor plans should be designed to ensure that all equipment functions together effectively without excessive special engineering or poor use of building space and services.

O2-10 [11]	Floor plans for equipment on raised floors should permit the removal of floor panels in the aisles without disturbing the equipment frames.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R2-5 [179], R2-7 [146] and R2-8 [147] and Objectives O2-6 [9], O2-9 [10] and O2-10 [11].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Vertical Space Allocation (2.3)

### Criteria:

O2-11 [13] 	Frames with their system cable racks should not exceed 2743 mm (9 ft) in height above the floor.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O2-11 [13].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Equipment Frame Floor Loading (2.3.2)

### Criteria:

O2-12 [18]	An individual frame should be limited to a floor load of 561 kg/m2 (115 lb/ft2).  The floor load for an equipment frame is calculated by dividing the frame weight by the area of a rectangle bounded by the extending frame sides and the center line of the standard front (nominal 762 mm [30 in]) and rear (610 mm or [24 in]) aisles.

R2-13 [19]	All overhead CDSs and lights located up to 3048 mm (10 ft) above the floor and having a maximum weight of 122.1 kg/m2 (25.0 lb/ft2) and shall be capable of being supported by equipment frames.  In partially equipped lineups, CDSs and lights may be partially supported by floor-mounted stanchions.  Over unequipped areas, via CDSs (defined in Section 2.6) may be supported by stanchions or from the ceiling.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O2-12 [18] and Requirement R2-13 [19].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Space Planning for Distributing Frames (DFs) (2.4)

### Criteria:

O2-14 [22] 	The vertical space from the floor up to 2743 mm (9 ft) is allocated for the DF and its associated system cabling, which includes all terminating cabling and racks. The space from 2743 mm to 3048 mm (9 to 10 ft) should be shared between the system and non-terminating via cabling. In long DF lineups, system cabling may be more than 2743 mm (9 ft), but must be less than 3505 mm (11 ft, 6 in) above the floor.

Failure to provide proper vertical allocation in the DF area will require special consideration to ensure the frame cabling will not interfere with via cabling, air ducts, or other building systems.

O2-15 [24] 	The overhead Cable Distribution Systems (CDSs) and lights within the DF area should be supported by the DF. In partially equipped lineups, cabling and lights may be supported by floor-mounted stanchions.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objectives O2-14 [22] and O2-15 [24].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Space Planning for Centralized DC Power Plant Equipment (2.5)

### Criteria:

R2-16 [25]	The vertical space allocated for centralized dc power plant equipment, including all superstructure and overhead facilities such as cable, cable racks, and bus bars, shall not exceed 3048 mm (10 ft).  This vertical space allocation also includes any vertical clearance (headroom) necessary for installation, operation, and maintenance.  Figure 2-6 shows a profile view of a typical centralized dc power plant equipment area.

O2-17 [27]	The floor loading in the centralized dc power plant equipment frame area should not exceed a total floor load capacity of  732 kg/m2 (150.0 lb/ft2).  Centralized dc power plant frames are allocated 684 kg/m2 (140.0 lb/ft2) with 48.8 kg/m2 (10.0 lb/ft2) allocated for transient loads.

O2-18 [28]	All overhead CDSs, bus bars, and lights in the centralized dc power plant equipment areas should be supported by the dc power plant equipment. In partially equipped areas, these elements may be supported by floor-mounted stanchions.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirement R2-16 [25] and Objectives O2-17 [27] and O2-18 [28].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Overhead Cable Distribution (2.6.1.2)

### Criteria:

O2-19 [29] 	At least one cross-aisle pathway per building bay should be reserved for via cabling.

O2-20 [30]	System and via lineup racks should be centered over the equipment lineups to minimize interference with installer access, and air and light distribution in the aisles.

O2-21 [31] 	System CDSs should be supported by the associated equipment frames/cabinets, or by stanchions in partially equipped lineups, with provision for inserting or removing frames/cabinets from a lineup. Via CDSs may be supported by the frames/cabinets or from the ceiling.

.

O2-22 [32]	System CDSs should be coordinated with frame-and-aisle lighting so the system conforms to the illumination requirements of Section 2.12, “Illumination of Equipment Spaces.”

O2-23 [33] 	System CDSs should provide adequate clearance for transporting frames in an erected position through the maintenance aisle.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objectives O2-19 [29], O2-20 [30], O2-21 [31], O2-22 [32] and O2-19 [29].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Cable Distribution Under Raised Floor (2.6.1.3)

### Criteria:

R2-24 [34]	Cabling under the raised floor shall conform to the requirements of the National Electric Code (NEC), i.e., NFPA 70, and applicable state and local codes.

R2-25 [35]	The under floor CDS shall provide for monitoring with smoke detectors and for protecting the cables against malfunctions caused by water leaks and dampness.

O2-26 [36]	Communication cables should be segregated from power cables to avoid physical damage and electrical interference.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R2-24 [34] and R2-25 [35] and Objective R2-26 [36].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## CDS Floor Load and Support (2.6.4)

### Criteria:

O2-27 [37]	The floor load from overhead CDSs (including lights) should not exceed 122.1 kg/m2 (25.0 lb/ft2).  The system CDSs are allocated 97.6 kg/m2 (20.0 lb/ft2) and via CDSs are allocated 24.4 kg/m2 (5.0 lb/ft2).  This weight allowance may be averaged over an area not exceeding 6.1-m (20-ft by 20-ft) square and must include all cable, rack, lights, and associated support hardware.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O2-27 [37].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## CEF Spatial Requirements (2.8.1)

### Criteria:

O2-28 [39]	Designs for the CEF should be compatible with the spatial requirements of the network, i.e., a 3048-mm (10-ft) clear height for equipment and associated cabling, and 3810 mm (12 ft, 6 in) for the lowest building structural member.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O2-28 [39].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## CEF Loading Requirements (2.8.2)

### Criteria:

O2-29 [40]	CEF equipment should have a maximum floor load of 700 kg/m2 (143.4 lb/ft2). This applies to floor-supported equipment, and is determined by totaling the weight of all such equipment in the area, including cable, splice cases, and racks, and dividing by the associated floor area. The total weight may be averaged over the entire cable entrance area, including aisles and personnel work areas. The weight of all such equipment should be supported by the floor.

R2-30 [41]	Wall-supported CEF equipment shall have a 366-kg/m2 (75.0-lb/ft2) maximum weight allowance. The uniform weight allocation is the total weight of CEF equipment divided by the surface area of the wall over which the equipment is placed. The center of gravity of any such wall-supported equipment shall be 406 mm (16 in) or less from the surface of the wall (measured perpendicular to the wall). Otherwise, the 366-kg/m2 (75.0-lb/ft2) weight allocation shall be proportionately decreased.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O2-29 [40] and Requirement R2-30 [41].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Quality of Light  (2.12.1.1)

### Criteria:

R2-31 [129]	CO lighting systems shall maintain the minimum levels of illumination in CO equipment areas according to Table 2-5.

O2-32 [130]	New lighting systems should provide initial illumination levels at least 25% higher (to account for losses due to lamp lumen depreciation and dirt accumulation in the luminaries), but no more than 50% higher (to account for modularity of the lighting equipment) than the levels listed in Table 2-5.

R2-33 [131]	The lighting system shall use energy efficient components (lamps, ballasts, etc.).

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Requirements R2-31 [129] and R2-33 [131] and Objective O2-32 [130].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Luminance Ratios (2.12.1.2)

### Criteria:

O2-34 [134]	The luminance of surfaces immediately adjacent to the visual task should be at least one-third that of the task, and should not exceed the luminance of the task. For more remote surfaces, the luminance of any significant surface normally viewed directly should be between one-third and five times the luminance of the task.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O2-34 [134].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

## Color of Light (2.12.1.3)

### Criteria:

O2-35 [135] 	In all new installations, fluorescent lamps should be used in equipment and operating areas because of their relatively high light output per watt. As a standard practice, it is recommended that fluorescent lamps with good color rendition be used.

### Test Location

The following evaluation was performed by (Engineer Name) between/on date(s) at the <ITL Name and Address>.

### Test Method

<<Describe test method in detail>>

<< Include any additional test conditions (e.g. line burner placement) from the NEBS Compliance Checklist which pertain to the environmental criteria>>

<<State if testing to the GR-63-CORE test method and describe any deviations from the GR documented test method>>

### Test Results

The <Product Name> is compliant/ not compliant with Objective O2-35 [135].

<<Describe test results in detail where relevant. Include graphs, tables, scans, chart recorder data, etc. of test results>>

<<Insert tables with detailed description of equipment pack fill>>