
[image: image1.png]verizon’




Network Equipment-Building Systems (NEBS)

Compliance Checklist

June 2018
Change Control Record:

	Version 
	Date
	Action*
	Reason for Revision

	1
	5/1/2004
	New
	New document.

	2
	8/11/2004
	Revised
	Added Power Drain and Return Current query to Power Requirements

	
	
	
	Added air filter query to Heat Release Requirements.

	
	
	
	Reworded sections H.2, H.3, H.6.  Added Sections H.19, H.20, H.21.

	3
	12/8/2004
	Revised
	Added GR-487 to list of documents in section 3.8.1.

	
	
	
	Added Earthquake Zone entry to section H.5

	4
	4/4/2006
	Revised
	Changes for SBC AT&T combination.

	5
	9/8/2006
	Change
	Modified to take into account the changes in the most recent revision of GR-63-CORE Issue 03; March 2006.

	
	9/8/2006
	Change
	Modified to take into account the changes in the most recent revision of GR-1089-CORE Issue 04; June 2006.

	
	9/14/2006
	Revised
	Added ANSI T1.336-2003 Requirements

	6
	11/4/2009
	Revised
	Modified to remove references to Bell South, update to cover GR-1089-CORE Issue 5 and made other minor editorial changes

	7
	04/2018
	Revised
	Updated to take into account the changes in the most recent revision of GR-63-CORE and GR-1089-CORE and other minor editorial changes 

	8
	06/2018
	Revised
	Updated with minor editorial changes

	* New, Add, Delete, Change, Revised


Prepared By:

	Name, Title, Organization 
	Date

	Signature on File

Verizon, Janette Bouché, PMTS, NEBS Compliance
	June 7, 2018


	Company, Contact 
	Date

	Signature on File

Verizon, Todd Talbot, DMTS, NEBS Compliance
	June 7, 2018


Verizon
 NEBS REQUIREMENTS

61.
WHY THE VERIZON NEBS COMPLIANCE CHECKLIST?

2.
NEBS INFORMATION
6
2.1.
OVERVIEW
6
2.2.
NEBS REQUIREMENTS
6
2.3.
DEFINITION OF REQUIREMENT AND OBJECTIVE
7
2.4.
SUBMISSION OF NEBS CHECKLIST APPENDIX B AND OTHER DATA
7
2.5.
TESTING COMPARED TO DESIGN INTENT
8
2.6.
OBTAINING NEBS REQUIREMENTS DOCUMENTS
8
2.7.
EQUIPMENT TESTING
10
2.8.
MAINTAINING NEBS COMPLIANCE
12
2.9.
COMPLIANCE REQUIREMENT
12
3.
WHERE TO REQUEST NEBS COMPLIANCE INFORMATION OR SEND NEBS CHECKLISTS, REPORTS AND DATA
13


APPENDIX A – Requirements Matrix

APPENDIX B - Test Report Certification

APPENDIX C – NEBS Compliance Checklist  

1. WHY THE VERIZON NEBS COMPLIANCE CHECKLIST?

1.1. All equipment deployed in Verizon’s Central Office (CO) equipment space or data rooms must be safe and pose no risk or safety hazard to any personnel, other nearby equipment or the physical structure.  Verizon also requires that equipment used for service to its customers must be able to deliver dependable and reliable performance during the conditions encountered under normal and abnormal circumstances.

1.2. Equipment compliance to Network Equipment Building Systems (NEBS) generic requirements and other recognized industry standards are the mechanisms used to provide this safety and reliability.  Some NEBS testing and design requirements help make the equipment operate properly and safely; other NEBS requirements enable lower initial and ongoing operating costs for Verizon.  

1.3. NEBS is recognized by financial risk assessors, municipalities and regulatory agencies as a major factor in Verizon’s ability to provide reliable, safe and cost efficient service to its customers.  Loss management and municipal agencies recognize the value of NEBS in reducing hazardous conditions and liability risks.  A lack of NEBS compliance could raise the cost of deployment of a given product a prohibitive amount.

1.4. The NEBS requirements allow Verizon to use a single, uniform set of rules to evaluate fairly and impartially all equipment to be placed in the central office environment – whether the equipment is owned by Verizon or placed in leased space by other companies.

1.5. The Verizon NEBS Compliance Checklist is a compendium of what Verizon believes are best industry practices, and do not necessarily reflect all carriers’ criteria or policies.  It is intended to help Verizon, equipment suppliers and independent testing laboratories by providing a first step toward a complete, common, standardized reference for NEBS compliance testing.   

2. NEBS INFORMATION

2.1. OVERVIEW

2.1.1. This document is intended to assist Verizon and CLEC suppliers in understanding and meeting NEBS requirements and to explain or clarify Verizon concerns and expectations.  
2.1.2. The NEBS requirements are described in GR-63-CORE, GR-1089-CORE, and GR-78-CORE.  

2.1.3. This document may be revised without notice.  The current version of this document is always available on the Verizon NEBS web page http://www.verizonnebs.com.
2.2. NEBS REQUIREMENTS

2.2.1. Verizon DOES NOT waive NEBS requirements.  All applicable requirements must be tested.  No test facility, supplier, or consultant may decide what requirements or objectives may be altered or omitted unless the Verizon’s NEBS compliance organization is consulted in advance. 

2.2.2. Verizon reserves the right to determine which requirements or objectives may or may not be required.  See Appendix A, Verizon’s NEBS Requirements.  Certain NEBS requirements may not be applicable for all equipment/systems under certain conditions.  

2.2.2.1. A detailed explanation the reason the requirement is not applicable shall be provided. 

2.2.2.2. Verizon’s NEBS compliance organization will determine the suitability of such explanations.

2.2.2.3. The final determination of all issues regarding applicability, pass/fail requirements or intent shall be decided by Verizon’s NEBS compliance organization.

2.2.3. All equipment that is being evaluated for NEBS compliance for use by Verizon or a collocator must meet the current NEBS requirements that are in effect at the time the equipment is being evaluated for deployment, not the time the equipment was tested.

2.3. DEFINITION OF REQUIREMENT AND OBJECTIVE

2.3.1. GR‑63, GR‑1089 and others list the required tests under the following designations: 

2.3.1.1. Mandatory Requirement (R): Testing is required; passing is required.

2.3.1.2. Objective (O) desired requirement: Testing is required; passing is the objective unless otherwise noted in this document.

2.3.1.3. Conditional Requirement (CR): Same as ‘Mandatory Requirement’, however, certain conditions as determined by the carrier may apply.

2.3.1.4. Conditional Objective (CO): Same as ‘Objective’, however, certain conditions as determined by the carrier may apply,

2.4. SUBMISSION OF NEBS CHECKLIST APPENDIX B AND OTHER DATA

2.4.1. Verizon may use the NEBS Compliance Checklist Appendix B to initiate assessment of equipment to be deployed within carrier network equipment space.
2.4.2. Product acceptance will be based on compliance of a supplier’s specific product to the requirements specified in Appendix A. 

2.4.3. Additional Verizon requirements, pass/fail criteria and clarifications are identified in the appropriate company specific documents listed in Table 2.

2.4.4. If used, the NEBS Compliance Checklist Appendix C, with all blanks filled in, and associated data and reports, shall be submitted by the supplier to Verizon's NEBS compliance organization.

2.4.4.1. The submitted form shall include an action plan and time schedule for any non-compliant results.

2.4.4.2. The Checklist Appendix C shall be completed using clear and concise wording and terminology. 

2.4.4.3. All blank spaces in the Appendix C shall be properly completed or filled in – no abbreviations shall be used.  Partial, incomplete or missing information on a submitted Appendix B will delay the analysis.

2.4.4.4. Pre-printed statements or measurement units may not be altered.  Additional information shall be submitted via additional pages as needed.

2.4.4.5. “Design Intent, Conforms by Design, Conforms by Analysis” and other similar phrases are generally considered to be ambiguous claims and are inadequate explanations.

2.4.4.6. Ambiguous abbreviations, e.g., N/A, shall be avoided when completing Appendix B.  If “Not Applicable” is used a detailed explanation is required.

2.4.4.7. Appendix C shall be submitted via e-mail to the carrier.

2.4.4.8. Appendix C shall be submitted with current data, as it is known at the time of submission. A supplemental or updated Appendix C may be submitted as additional data becomes available.  It is the responsibility of the supplier to ensure that supplemental Appendix C submissions and test reports are provided in a timely manner to the carrier NEBS compliance organization.  A supplemental or updated Appendix C may be provided as work progresses and shall clearly indicate new or changed information. New or additional data shall be clearly, e.g., bold, italic, highlighted, color, etc., noted on the subsequent submittals.  

2.4.4.9. All test data and lab reports submitted to Verizon shall be preceded or accompanied by a current version of the Carrier NEBS Compliance Checklist Appendix B.

2.4.4.10. Any Appendix C received that does not include the specific project or application for the product and a NEBS contact person for the product will be considered to be unsolicited material and may not be reviewed.  Please note that members of the NEBS Compliance team are not the carrier contact interested in using the product. 

2.4.4.11. The NEBS Compliance Checklist Appendix B, Item A - Project Application/Description shall indicate the intended application/location for the equipment installed in Verizon’s facilities.  For example, the Item A shall indicate if the HOST/REMOTE, COT/RT, etc. equipment will be installed in carrier CO space.

2.4.4.12. Only the Appendix B, not this entire document, fully and properly completed shall be submitted. Any blank space is generally considered to be missing data.

2.4.5. Test Report Certification.  A completed Test Report Certification, Appendix B, must be attached to each test report.  Verizon will not accept test reports without accurate and complete certifications.  Please direct any questions to Verizon’s NEBS compliance contact.  Submit reports and certifications to Verizon’s NEBS compliance organization per Section 3.

2.4.6. Laboratory test reports and videos shall be provided upon completion of testing.  All reports shall be provided in digitized form.  

2.4.7. The Verizon NEBS compliance organization will review the Appendix C and all supporting data to determine product acceptability based solely on Verizon’s NEBS compliance organization’s interpretation of the intent of the applicable requirements. 

2.4.8. Verizon’s NEBS compliance organization may work directly with the supplier to resolve any compliance issues identified in the data provided.
2.5. TESTING COMPARED TO DESIGN INTENT

2.5.1. Testing is required to prove compliance with NEBS Requirements.  Compliance statements are inadequate without test results or other substantiating information that is acceptable to Verizon’s NEBS compliance organization.

2.5.2. Under circumstances, as agreed upon by Verizon’s NEBS compliance organization, Verizon may accept certain field experience data.

2.5.3. The level of compliance of the equipment will be determined upon receipt of the required test data.

2.5.4. If tests are in progress or planned, a Checklist must be provided and show expected completion dates.

2.6. OBTAINING NEBS REQUIREMENTS DOCUMENTS

2.6.1.      The equipment supplier is expected to obtain the necessary copies of the documents listed below:  

	Telcordia Documents (Latest issues apply)

	GR-63
	NEBS™ Requirements: Physical Protection-Generic Equipment Requirements

-Describes Physical Requirements

	
	

	GR-1089
	Electromagnetic Compatibility and Electrical Safety Generic Criteria for Network Telecommunication Equipment: 

-Describes EMC, ESD, and Electrical Safety Requirements

	
	

	GR-78 
	Generic Physical Design Requirements for Telecommunications Products and Equipment:

-Describes General Manufacturing Techniques for Equipment Reliability (e.g., connector types; contact mating surfaces; mixed metal avoidance; tin whisker avoidance; circuit trace sizing and spacing; component materials and composition). 

	GR-487 
	Generic Requirements for Electronic Equipment Cabinets:

-Generic requirements for electronic equipment and broadband cabinets.

	GR-3028 
	Thermal Management In Telecommunications Central Offices:

 -Provides thermal management information, guidelines, targets, Objectives, and Requirements for equipment manufacturers and service providers for ensuring network integrity.



	SR-3580 
	Network Equipment - Building Systems (NEBS) Criteria Levels:

-Telcordia grouping of proposed of the proposed generic requirements into functional groups or levels.


	GR 295 
	Mesh and Isolated Bonding Networks: Definition and Application to Telephone Central Offices


	GR 357 
	Generic Requirements for Assuring the Reliability of Components Used in Telecommunications Equipment.  


	Visit the Telcordia store, http://telecom-info.telcordia.com/site-cgi/ido/index.html, or contact Ericsson Customer Service Center at One Ericsson Drive, Piscataway, NJ 08854‑4156, 844-251-0201 for further information.

	


Table 1

2.6.2. The document listed below provides Verizon specific clarifications to NEBS testing and evaluation process.  The equipment supplier is expected to obtain copies of the document listed below as necessary:  

	Verizon Clarification Documents:  VZ.TPR.9305

	Visit the Verizon NEBS Compliance Web Page at http://www.verizonnebs.com/.


Table 2.

2.7. EQUIPMENT TESTING

2.7.1. TEST FACILITY AND CHARGES

2.7.1.1. The supplier shall be responsible for all costs/charges associated with compliance testing.  

2.7.2. TEST DOCUMENTATION

2.7.2.1. The NEBS Compliance Checklist Appendix C is a vehicle for reporting product and testing information, but is not accepted without supporting test data.

2.7.2.2. The supplier must furnish sufficient documentation to substantiate to Verizon’s NEBS compliance organization that NEBS testing was done per the stipulated procedures, methods, and ranges in the NEBS family of documents, referenced in Section 2.6.1.

2.7.2.3. Suppliers shall ensure that the selected test facility is familiar with the documentation criteria noted throughout this document and is acceptable to Verizon’s NEBS compliance organization

2.7.2.4. Verizon NEBS compliance organization will not return test reports and videos.

2.7.2.5. Lab reports, written documentation, fire spread and earthquake videos, etc. shall specifically reference the appropriate GR‑63, GR‑1089, GR-78 section(s) covered by the report.

2.7.2.6. Lab reports shall specifically report test results by referencing the appropriate GR Requirement (R) or Objective (O) numbers.  Paragraph numbers are optional.  

2.7.2.7. Lab reports and documentation shall report test conditions and observed characteristics of the equipment during testing.  Explanations of conditions and reactions shall be included as appropriate, including descriptions of failures and errors and the impact on the functional performance of the equipment.  Reports shall refrain from injecting opinions into the body of the observations.  Opinions may be grouped together in a specifically labeled report section.

2.7.2.8. Tested equipment configurations and a list of all equipment modules used in the test configurations shall be included.  The list shall include the module name/designation, model number, and part/ordering number. Any equipment modules not used in a tested configuration shall be listed as not tested.

2.7.2.9. Test data, reports, and videos shall be submitted complete and intact, that is, as originally provided by the test facility.  Reports that are missing information or are re-packaged by a supplier may not be acceptable.

2.7.2.10. Suppliers and lab facilities are reminded that a Root Cause Analysis (RCA) is required for all tests that have failed, including those of GR-63-CORE, GR-1089-CORE and the tests specified in this document, even if subsequent re-testing is successful. (GR‑63; R4‑1, R4‑2)

2.7.2.11. RCAs must include an explanation of what failed, why it failed (i.e., what caused the cause of the failure) and corrective action description.  

2.7.2.12. Manufacturing cut-in dates, serial numbers, product ID changes, ordering requirements, availability, etc. for equipment incorporating the corrective action shall be included in RCAs.

2.7.3. TEST METHODS or PROTOCOLS

2.7.3.1. The NEBS Generic Requirements documents describe the procedures, methods and range criteria to be used to do the NEBS tests and the acceptable test result limits.  Suppliers and test labs are cautioned not to omit or modify portions of the test(s) without Verizon’s NEBS compliance organization’s prior agreement.

2.7.3.2. Compliance requires that the tests be performed as described in GR‑63 and GR‑1089 or other specifications and that the results meet the described limits.

2.7.3.3. Many of the various elements have multiple subsections and criteria.  If any of these subsections do not fully conform to the requirements, the entire section does not conform.  The supplier shall report data by subsection if necessary.

2.7.3.4. Suppliers and test labs are cautioned not to abort a test in progress simply because a segment or requirement failed to pass.  The errors, failure mode, symptoms and performance shall be documented in the report.  The failure mode and data are important in analyzing the ability of the equipment to function under the potential marginal conditions represented by the test.

2.7.3.5. Suppliers’ or manufacturers’ internal corporate standards and requirements are generally considered to be insufficient as a gating pass/fail requirement.  Use of these standards requires prior agreement with Verizon’s NEBS compliance organization and the standards must fully and specifically reference the NEBS family of documents.  

2.7.4. SUPPLIER ACTION PLANS

2.7.4.1. For elements that “CONFORM,” provide a copy of the laboratory test data.

2.7.4.2. For elements that “FAIL to CONFORM,” provide a copy of the laboratory test data, an action plan and an explanation indicating when and how Compliance will be attained.

2.7.4.3. For elements that “PARTIALLY CONFORM,” provide a copy of the laboratory test data, an action plan and an explanation indicating when and how compliance will be attained.

2.7.4.4. Suppliers or manufactures shall provide detailed explanations of the reason any elements were not tested.  In general, all elements must be tested; however, there may be specific circumstances where testing may not be required.

2.7.5. EQUIPMENT CONFIGURATION

2.7.5.1. Suppliers shall ensure that the equipment to be tested is arranged so that all equipment slots or positions, e.g., circuit pack slots, are fully equipped to a worst case configuration with regard to floor load, heat release, fire resistance, fuel load, etc. The configuration shall include all representative circuit packs likely to be used or encountered by Verizon, even if the slot normally contains a circuit pack that is not being evaluated as part of the current test sequence.   Once the configuration intended for the carrier is reached, the supplier may add additional PCBs that could be used in the equipment for different applications.

2.7.5.2. Refer to GR‑1089, Section 3.5.5.3.3 “The EUT power and signal leads shall be, as nearly as possible, of the same length, orientation, and termination as they are in their normal operational configuration.”

2.7.5.3. Equipment shall be functioning, except for the fire spread tests, using acceptable call processing, application or load generating software that simulates normal traffic or operational loads.  Diagnostic exercises are generally not sufficient.

2.7.5.4. Equipment may not be functionally tested at a unit or shelf level unless it can properly perform the intended deployed function and is representative of the installed configurations likely to be encountered. Specifically, multi-shelf systems (e.g., a control unit and the units controlled) shall be tested at the frame level.

2.7.5.5. All workstations, terminals, monitors, modems, alarm units, ringing and tone generators, etc. that may be required for the equipment being tested and are permanently installed, i.e., ‘left in place,’ shall be included in the equipment test configurations.

2.7.5.6. Suppliers are encouraged to verify test plans and configurations with the Verizon’s NEBS compliance organization before tests are done, to ensure the test configurations will be acceptable to the carrier.  Test plans shall list all tests, provide detailed card layouts and indicate test points.  If a test is not being performed, it shall still be listed and an explanation provided of why the test is not being performed.

2.7.5.7. If a supplier has a shelf level product but anticipates that multiple units will be used in a specific application, then the appropriate number of units shall be placed in a rack and tested together as a system.  The carrier may not accept individually tested shelf units when they are combined with other like or different shelves for a specific application.

2.7.5.8. All supplier provided racks, frames and cabinets must be of welded, steel construction and meet the specifications of GR-63 section 3. 

2.7.6. OEM EQUIPMENT

2.7.6.1. The equipment supplier is responsible for ensuring that all OEM (Original Equipment Manufacturer) devices and subassemblies also meet the NEBS requirements.

2.7.6.2. The use of an OEM component or subsystem as a part of the larger system/application does not relieve any NEBS criteria.

2.7.6.3. The supplier or integrator of the final system or application provided to the carrier is responsible for attaining and maintaining NEBS Compliance.

2.7.6.4. The supplier or integrator of the final system or application provided to the carrier may provide the OEM’s test data if authorized by the OEM.  However, if the OEM equipment is integrated in a rack configuration with other equipment, the entire configuration must be NEBS tested.

2.8. MAINTAINING NEBS COMPLIANCE

2.8.1. The supplier is responsible for ensuring that NEBS Compliance is maintained throughout the equipment’s deployed service life.  Specifically, it is the supplier’s responsibility to ensure that replacement repaired or redesigned parts continues to meet the NEBS requirements.  The NEBS checklist Appendix C shall be resubmitted after every NEBS effecting change as determined by an ITL.  Examples of possible NEBS effecting changes include microprocessor changes, printed circuit board changes, component modifications and substitutions, back-plane modifications, enclosure modifications, etc. 

2.9. COMPLIANCE REQUIREMENT 

2.9.1. Lack of substantiating data, as described in this document, will be considered non‑compliance.  All equipment considered for deployment in Verizon Central Office equipment space will be evaluated based on compliance to all NEBS requirements.  See Section 2.2.

2.9.2. NEBS compliance must be demonstrated by testing to the requirements in GR‑63‑CORE, GR‑1089‑CORE and requirements as noted in Appendix B.  These documents describe the test methods and procedures and the expected test result limits.

2.9.3. No supplier or test facility shall base compliance on the use of a cabinet or enclosure to contain EMI or fire spread.  That is, cabinets shall not be relied upon to act as a barrier.  The equipment must meet the requirements.  Under certain conditions, Verizon’s NEBS compliance organization may prescribe the use of such cabinetry only as a (limited) mitigation measure.

2.9.4. The supplier is expected to maintain NEBS Compliance for the product, throughout the equipment service life, as described in GR 357. 

WHERE TO REQUEST NEBS COMPLIANCE INFORMATION OR SEND NEBS CHECKLISTS, REPORTS AND DATA

All requests for NEBS compliance information or checklists shall be sent to the contact listed below or as provided by Verizon.  E-mailing a checklist will expedite analysis.

Verizon

Todd Talbot,

DMTS, Verizon Maintenance Engineering
320 St. Paul Place
Baltimore, MD 21202

Tel:  410-736-5945 

E-mail: todd.f.talbot@verizon.com
3. APPENDIX A.












Requirements Matrix

A:  General Information

The following matrices list the various GR-63-CORE and GR-1089-CORE requirements and objectives followed by columns listing each company’s specific comments.  The company specific comments can be interpreted according to the following key.

	EC
	Evaluation Clarification Required (See VZ.TPR.9305)

	ENR
	Evaluation Not Required

	ER
	Evaluation Required

	TBD
	To Be Determined


B:  GR-63-CORE Requirements, Issue 5, December 2017
	Section
	Section Name
	Criteria
	Key

	2
	Facility and Space Planning Requirements
	-
	-

	  2.1
	Equipment Frames Conformity
	-
	-

	
	  Side to side lineup
	R2-1 [178]
	ENR

	
	 One Depth
	O2-2[4]
	ENR

	
	  Alignment
	O2-3 [7]
	ENR

	
	  Clearance
	O2-4 [8]
	ENR

	 2.2
	Floor Plans
	-
	-

	
	 Back-to-Back Lineup
	R2-5 [179]
	ENR

	
	  Floor Plans
	O2-6 [9]
	ENR

	
	  Maximum Aisle Spacing
	R2-7 [146]
	ENR

	
	  Minimum Main Aisle Spacing
	R2-8 [147]
	ENR

	
	  Equipment Functionality
	O2-9 [10]
	ENR

	
	  Raised Floors
	O2-10 [11]
	ENR

	2.3
	Vertical Space Allocation
	-
	-

	
	  Maximum Height
	O2-11 [13]
	ER

	2.3.2
	Equipment Frame Floor Loading
	-
	-

	
	  Equipment Frame Floor Loading
	O2-12 [18]
	ER

	
	  Overhead CDS
	R2-13 [19]
	ER

	2.4
	Space Planning-Distributing Frames
	-
	-

	
	 Vertical  Frame Dimension
	O2-14 [22]
	ER

	
	  Overhead Cable
	O2-15 [24]
	ER

	2.5
	DC Power Plant Equipment
	-
	-

	
	  DC Power Height
	R2-16 [25]
	ER

	
	  Frame Floor Load
	O2-17 [27]
	ER

	
	  Power CDS Structure
	O2-18 [28]
	ER

	2.6
	Cable Distribution Systems (CDSs)
	-
	-

	2.6.1.2
	Overhead Cable Distribution
	-
	-

	
	  Cross Aisle path
	O2-19 [29]
	ENR

	
	  Centering
	O2-20 [30]
	ENR

	
	  Support of Assoc Equipment
	O2-21 [31]
	ENR

	
	  Illumination Requirements
	O2-22 [32]
	ENR

	
	  System CDS Clearance
	O2-23 [33]
	ENR

	2.6.1.3
	Cable Distribution Under Raised Floor
	-
	-

	
	  Under floor Cabling NEC
	R2-24 [34]
	ENR

	
	  Under floor CDS
	R2-25 [35]
	ENR

	
	  Cable Segregation
	O2-26 [36]
	ENR

	2.6.4
	CDS Floor Load and Support
	-
	-

	
	  CDS Floor Load and Support
	O2-27[37]
	ER

	2.8
	Cable Entrance Facility (CEF)
	-
	-

	2.8.1
	CEF Spatial Requirements
	-
	-

	
	  CEF Spatial Requirements
	O2-28[39]
	ENR

	2.8.2
	CEF Loading Requirements
	-
	-

	
	  Floor Loading Requirements
	O2-29 [40]
	ENR

	
	  Wall-Supported Weight Limit
	R2-30 [41]
	ENR

	2.12
	Illumination of Equipment Spaces
	-
	-

	2.12.1
	Central Office Lighting Systems
	-
	-

	2.12.1.1
	Quantity of Light
	-
	-

	
	  Minimum Levels of Illuminations
	R2-31 [129]
	ENR

	
	  Illumination Level
	O2-32 [130]
	ENR

	
	  Energy Efficient Lighting System
	R2-33 [131]
	ENR

	2.12.1.2
	Luminance Ratios
	-
	-

	
	   Luminance Ratios
	O2-34 [134]
	ER

	2.12.1.3
	Color of Light
	-
	-

	
	   Color of Light
	O2-35 [135]
	ENR

	3
	Equipment Spatial Design Requirements
	-
	-

	
	Horizontal extension
	R3-1 [5]
	ER

	3.2
	Equipment Frame Floor Mounting
	-
	-

	
	  Hole Pattern
	R3-2 [1]
	ER

	
	  Anchoring Method
	R3-3 [2]
	ER

	
	  Torque 
	R3-4 [180]
	ER

	
	  Anchor Bolt System
	R3-5 [181]
	ER

	
	  Leveling capabilities
	R3-6 [6]
	ER

	3.3
	Junctioning
	-
	-

	
	  Junctioning to adjacent frames
	R3-7 [182]
	ER

	3.4
	Frame Dimensions
	-
	-

	
	  Drawings
	R3-8 [183]
	ER

	3.4.1
	Open Style Racks
	-
	-

	
	  Open Rack HxWxD
	03-9 [14]
	ER

	
	  Depth Specification
	03-10 [148]
	ER

	3.4.2
	Other Rack Styles
	-
	-

	
	  HxWxD, New Equip or Deeper Chassis
	03-11 [150]
	ER

	3.4.3
	Shipping
	-
	-

	
	 Equipment Entrance
	R3-12 [3]
	ER

	3.4.4
	Equipment Frame End Guards
	-
	-

	
	   Equipment Frame Lineup Conformity 
	R3-13 [17]
	ER

	3.5
	Equipment Frame Cable Management Provisions
	-
	-

	
	  Cabling Access
	R3-14 [151]
	ER

	
	  Larger Cable Management
	O3-15 [152]
	ER

	
	 Segreating Power Cables
	03-16 [184]
	ER

	3.5.1
	Equipment Frame Interface with Cable Rack
	-
	-

	
	   Fastening Arrangement
	R3-17 [15]
	ER

	
	   Framework
	O3-18 [16]
	ER

	
	   Bend Radius for Fiber During Transition
	R3-19 [185]
	ER

	3.7
	Equipment Frame Support of CDS and Lights
	R3-20 [186]
	ER

	3.8
	AC Convenience Outlets Within Equipment Frames
	-
	-

	
	   AC Convenience Outlets
	R3-21 [20]
	ER

	
	   National Electric Code (NEC)
	R3-22 [21]
	ER

	3.9
	Other Frame Types
	-
	-

	3.9.1
	  Distributing Frames (DFs)
	-
	-

	
	    Maximum Height
	O3-23 [187]
	ER

	
	    Frame Floor Load
	R3-24 [23]
	ER

	
	    Overhead CDS and Light Support
	O3-25 [188]
	ER

	3.10
	DC Power Equipment Frames
	-
	-

	
	  Vertical Space Allocation
	R3-26 [189]
	ER

	
	   Floor Load Capacity
	O3-27 [190]
	ER

	
	   Support for Overhead Elements
	O3-28 [191]
	ER

	3.11
	Equipment Chassis Mounting
	-
	-

	
	   Chassis Attachment
	R3-29 [192]
	ER

	
	    Fastening Arrangement
	O3-30 [149]
	ER

	
	   Circuit Pack Retention
	R3-31 [193]
	ER

	4.0
	Environmental Criteria
	-
	-

	
	  RCA 
	R4-1 [67]
	ER

	
	  RCA solution
	R4-2 [68]
	ER

	4.1
	Temperature, Humidity, and Altitude Criteria
	-
	-

	4.1.1
	Transportation and Storage Environmental Criteria
	-
	-

	4.1.1.1
	Low-Temperature Exposure and Thermal Shock
	R4-3 [69]
	ER

	4.1.1.2
	High Relative Humidity Exposure 
	R4-4 [71]
	ER

	4.1.1.3
	High-Temperature Exposure and Thermal Shock
	R4-5 [70]
	ER

	4.1.2
	Operating Temperature and Humidity Criteria
	-
	-

	
	  Ambient Temperature and Humidity Limits
	R4-6 [72]
	ER

	4.1.3
	Altitude
	-
	-

	
	  Altitude to 6000
	R4-7 [74]
	ER

	
	  Altitude to 13,000
	R4-8 [136]
	ER

	
	  Criteria above 6000
	R4-9 [75]
	ER

	
	  Functional to 6000
	O4-10 [137]
	ER

	
	  Functional to 13,000
	O4-11 [76]
	ER

	4.1.4
	Temperature Margin Evaluation
	-
	-

	
	  Temperature Response
	R4-12 [153]
	ER

	4.1.5
	Fan Cooled Equipment Criteria
	-
	-

	4.1.5.1
	Equipment Fan Performance Criteria
	-
	-

	
	  Single Fan Failure
	R4-13 [154]
	ER

	
	  Remote Alarm
	R4-14 [155]
	ER

	
	  Cooling Unit Replacement
	O4-15 [156]
	ER

	
	  Replacement Proc. In Documentation
	R4-16 [157]
	ER

	
	  Service Interruption 
	R4-17 [158]
	ER

	4.1.5.2
	Equipment Fan-Filter Criteria
	-
	-

	
	  Fan Filters
	R4-18 [138]
	ER

	
	  Filters for 1RU Equipment
	O4-19 [206]
	ER

	
	  Fan Filters Dust Spec
	R4-20 [139]
	ER

	
	  Fan Filter for 2U equipment
	R4-21 [176]
	ER

	
	Fan Filter Minimum Fire Rating
	R4-22 [140]
	ER

	
	Air Bypass
	R4-23 [141]
	ER

	
	  Handling Contamination
	R4-24[142]
	ER

	
	  Replacement Schedule
	R4-25 [143]
	ER

	
	  Filter Alarm
	O4-26[144]
	ER

	
	  Filter Disposable
	R4-27[145]
	ER

	
	Recyclable Materials
	04-28 [194]
	ER

	4.1.6
	Heat Dissipation and Energy Efficiency
	-
	-

	
	  Maximum Heat Release and Cooling   Method
	R4-29 [77]
	ER

	
	   Heat Release
	O4-30[78]
	ER

	
	   DC Power Plant Compatibility
	04-31[195]
	ER

	
	   TEEER Testing
	R4-32 [196]
	ER

	4.1.7
	Surface Temperature
	-
	-

	
	  Aisle Facing Surfaces (per Table)
	R4-33 [159]
	ER

	4.1.8
	Equipment Airflow
	-
	-

	
	  Airflow Schemes (approved)
	R4-34 [160]
	ER

	
	  Airflow Schemes (not approved)
	04-35 [161]
	ER

	
	   Baffles/Deflectors
	O4-36 [197]
	ER

	
	   Testing Requirements for Baffles
	R4-37 [198]
	ER

	
	Equipment with other than front aisle air inlet
	R4-38 [199]
	ER

	4.2
	Fire Resistance
	-
	-

	4.2.2
	Equipment Assembly Fire Tests
	-
	-

	4.2.2.1
	Frame-Level Fire-Resistance Criteria
	-
	-

	
	A.  Fire spread Criteria
	-
	-

	
	      Flame Spread
	R4-39 [81]
	EC

	
	      Excessive Surface Burning
	R4-40[162]
	ER

	
	B.  Fire Propagation Hazard Characterization
	-
	-

	
	     Rate Of Heat Release
	R4-41 [82]
	ER

	
	       Peak Heat Release
	O4-42 [83]
	EC

	
	       Average Heat Release
	O4-43 [84]
	EC

	
	       Flame Spread without Fans
	04-44 [200]
	EC

	4.2.2.2
	Shelf-Level Fire-Resistance Criteria
	-
	-

	
	  A. Fire spread Criteria
	-
	-

	
	        Flame Spread
	R4-45 [86]
	EC

	
	        Excessive Surface Burning
	R4-46 [163]
	ER

	
	  B. Fire Propagation Hazard Characterization
	-
	-

	
	     Rate Of Heat Release
	R4-47 [87]
	EC

	
	       Peak Heat Release
	O4-48 [88]
	EC

	
	       Average Heat Release
	O4-49 [89]
	EC

	
	       Flame Spread Without Fans
	04-50 [201]
	EC

	4.2.2.3
	Smoke and Self-Extinguishment Criteria
	-
	-

	
	  4min 30sec., Start to Self-Extinguish
	O4-51 [164]
	ER

	
	  10min, Flame Reduction
	O4-52[165]
	ER

	
	  15min, Flames Extinguished
	R4-53 [166]
	ER

	
	  15min, Minimal Wisps of Smoke
	O4-54 [167]
	ER

	
	  20min, No Visible Smoke
	R4-55 [168]
	ER

	
	   Unpowered Fan Testing
	O4-56 [202]
	EC

	4.2.3
	Use of Fire-Resistant Materials, Components, Wiring, and Cable
	-
	-

	4.2.3.1
	Material/Comp. Fire-Resistance Criteria
	-
	-

	
	  Fire Resistance
	R4-57 [90]
	ER

	4.2.4
	Use of Fire-Resistant Materials for Battery Systems
	
	

	
	Structural Materials within Battery Systems
	R4-58 [207]
	ER

	
	Flash Point
	04-59 [208]
	ER

	
	Fire Resistance
	R4-60 [209]
	ER

	
	Listing
	R4-61 [210]
	ER

	4.3
	Equipment Handling Criteria
	-
	-

	4.3.1
	Packaged Equipment Shock Criteria
	-
	-

	4.3.1.1
	Category A Containers
	R4-62 [107]
	ER

	4.3.1.2
	Category B Containers
	R4-63 [108]
	ER

	4.3.2
	Unpackaged Equipment Shock Criteria
	R4-64 [109]
	ER

	4.4
	Earthquake, Office Vibration, and Transportation Vibration
	-
	-

	4.4.1
	Earthquake Environment and Criteria
	-
	-

	
	  Waveform Testing per 5.1
	R4-65[110]
	ER

	
	  Amplitude Deflection
	R4-66[111]
	ER

	
	  Natural Mechanical Frequency >2.0 Hz
	R4-67 [112]
	ER

	
	  Natural Mechanical Frequency > 6.0 Hz
	O4-68 [113]
	ER

	
	  Axis Waveform Testing
	R4-69 [114]
	ER

	
	  Functional Operation
	O4-70 [115]
	ER

	4.4.2
	Framework and Anchor Criteria
	-
	-

	
	  Welded Construction
	O4-71[116]
	ER

	
	  Base Mounting
	R4-72 [117]
	ER

	
	  Static Pull
	O4-73 [118]
	ER

	
	  Concrete Anchors (max depth)
	R4-74 [119]
	ER

	
	  Concrete Anchors (dynamic applications)
	O4-75 [120]
	ER

	
	  Steel Anchors
	O4-76 [121]
	ER

	4.4.3
	Wall-Mounted Equipment Anchor Criterion
	-
	-

	
	Welded Construction
	04-77 [211]
	ER

	
	  Fasteners Load criteria
	R4-78 [175]
	ER

	4.4.4
	Office Vibration Environment and Criteria
	-
	-

	
	  Physical Performance Criteria
	R4-79[122]
	ER

	
	  Functional Performance Criteria
	R4-80 [123]
	ER

	4.4.5
	Transportation Vibration Criteria
	R4-81 [124]
	ER

	4.5
	Airborne Contaminants
	-
	-

	4.5.2
	Contamination Levels
	-
	-

	4.5.2.1
	Environmentally Controlled Space
	R4-82 [125]
	ER

	4.5.2.2
	Outside Plant Equipment
	R4-83 [127]
	ER

	4.6
	Acoustic Noise
	-
	-

	
	  Acoustical noise Limits
	R4-84 [128]
	ER

	
	  Fan Sound Power Level
	R4-85 [177]
	ER

	4.7
	Illumination
	-
	-

	4.7.2
	Illumination Criteria for Network Equipment
	-
	-

	
	  Surface Reflectance and Color
	O4-86 [132]
	ER

	
	  Glare
	O4-87 [133]
	ER


C:  GR-1089-CORE Requirements, Issue 7, February 2018
	Section
	Section Name
	Criteria
	Verizon

	1.9
	Documentation
	-
	-

	1.9.1
	General
	-
	-

	
	  Port Type
	R1-1 [153]
	ER

	
	 Cautions and Warnings
	R1-2 [154]
	ER

	
	 Installation and Maint. Documentation
	R1-3 [155]
	ER

	
	 Testing Not Applicable
	R1-4 [156]
	ER

	1.9.2
	Root Cause Analysis (RCA)
	-
	-

	
	  RCA Performance Requirement
	R1-5 [157]
	ER

	
	  RCA Resolution
	R1-6 [158]
	ER

	2
	System-Level Electrostatic Discharge
	-
	-

	2.1.2
	 ESD Immunity Criteria
	-
	-

	
	Test to Normal and Inst/Maintenance
	R2-2 [2]
	ER

	2.1.2.1
	Immunity Criteria – Normal Operation
	R2-3 [3]
	ER

	2.1.2.2
	Immunity Criteria – Installation and Repair
	R2-4 [4]
	ER

	2.1.2.3
	ESD Warning Label Requirements
	R2-5 [5]
	ER

	2.1.2.4
	Equipment Specific Requirements
	-
	-

	
	  Additional Equipment Requirements
	R2-6 [6]
	ER

	
	  Maintenance Information
	R2-7 [7]
	ER

	2.2
	Electrical Fast Transient
	R2-8 [126]
	ER

	3
	Electromagnetic Interference
	-
	-

	3.1.5
	Documentation
	R3-1 [159]
	ER

	3.2.1.1
	Electric Fields Radiated Emission Criteria
	-
	-

	
	  Closed Door Requirement
	R3-2 [8]
	ER

	
	  Open Door Objective
	O3-3 [9]
	ER

	
	  Open Door Requirement
	R3-4 [10]
	ER

	3.2.1.2
	Electric Fields Radiated Emission Criteria for Intentional Radiators
	-
	-

	
	  Certified to parts of 47 CFR
	R3-5 [160]
	ER

	
	  Closed Door Requirement
	R3-6 [161]
	ER

	
	  Fund. Freq. Measurement in Report
	R3-7 [162]
	ER

	
	  Open Door Objective
	O3-8 [163]
	ER

	3.2.2.1
	Conducted Emission Requirements for AC Power Ports – Voltage
	R3-9[12]
	ER

	3.2..2.2
	Conducted Emission Requirements for AC and DC Power Ports – Current
	R3-10 [13]
	ER

	3.2.3
	Conducted Emission Criteria for Telecommunications Ports
	-
	-

	
	Conducted Emissions Requirements for Signal Leads – Current
	R3-11 [128]
	ER

	3.3
	Immunity Criteria
	
	

	3.3.1
	Radiated Immunity Criteria
	-
	-

	3.3.1.1
	Electric Fields Radiated Immunity Criteria with Doors and Covers Closed
	-
	-

	
	  Doors and Covers Closed
	R3-12[16]
	ER

	3.3.1.2
	Electric Fields Radiated Immunity Criteria with Doors and Covers Open
	-
	-

	
	Calibrated Fields
	R3-13[18]
	ER

	3.3.2
	Conducted Immunity Criteria for AC and DC Power Ports
	-
	-

	
	  Longitudinal Injection
	R3-14 [130]
	ER

	3.3.3.1
	Conducted Immunity Requirement for Signal Leads
	R3-15 [131]
	ER

	3.3.3.2
	Conducted Immunity Objectives for Voiceband and Telecommunications Leads
	R3-16 [164]
	ER

	4
	Lightning and AC Power Fault
	-
	-

	4.1
	Port Classification
	R4-1 [231]
	ER

	4.2
	Electrical Protection on Coaxial and Paired Conductor Systems
	-
	-

	4.2.2
	Current-Limiting Protectors
	R4-2 [232]
	ER

	4.5
	General Testing Information and Guidelines
	
	

	4.5.1
	Test Generator Compliance
	R4-3 [26]
	ER

	4.5.9
	Equipment Interfacing with Agreed or Non-Field Replaceable Integrated Primary Protectors
	
	

	
	Specify Primary Protector
	R4-4 [179]
	ER

	
	Documentation/Warning Requirement
	R4-5 [181]
	ER

	
	Document recovery time
	R4-6 [251]
	ER

	
	Typical Approximate Boot Time
	R4-7 [252]
	ER

	4.6
	Testing Requirements
	-
	-

	4.6.1.1
	Short Circuit Test (Type 1,3,5,Ports)
	R4-8[25]
	ER

	4.6.1.2
	Ethernet Ports
	R4-9 [233]
	ER

	4.6.1.3
	Cell Site (Type 3a/5a and 8b Ports)
	R4-10 [234]
	ER

	4.6.2
	Lightning Requirements and Test Criteria
	-
	-

	4.6.2.1.1
	First-Level Lightning Criteria (Telecommunications Type 1,3, 3b/5b and 5  Ports)
	-
	-

	
	  OSP Lightning Surges
	R4-11[27]
	ER

	
	  Secondary Protector Test
	R4-12 [167]
	ER

	
	  Exempt Circuit Pack Labels
	R4-13 [236]
	ER

	4.6.2.1.2.7
	High Exposure Residential (Type 3 and 5 Ports)
	CO4-14 [178]
	ER

	4.6.2.1.3
	Intra-Building or Intra-Site Lightning Criteria
	-
	-

	
	Ports Connected to Unshielded Cables
	R4-15 [30]
	ER

	
	Equipment Ports With Secondary Protection
	R4-16 [169]
	ER

	
	Intra-Building Port Warning Requirement
	R4-17 [31]
	ER

	
	Ports with Shielded Cables
	R4-18 [170]
	ER

	
	Ports with Shielded Cable Warning
	R4-19 [237]
	ER

	4.6.2.1.5
	First Level Lightning Criteria for Antenna Ports
	-
	-

	
	  Type 6 Port Testing
	R4-20 [209]
	ER

	
	  Ports With Secondary Protection
	R4-21 [238]
	ER

	4.6.2.1.6
	First Level Lightning Criteria for AC Power Ports
	-
	-

	
	  Surge Protective Device (SPD)       Documentation
	R4-22 [210]
	ER

	
	  Ports with External SPD
	R4-23 [32]
	ER

	
	  Ports Without External SPDs
	R4-24 [211]
	ER

	4.6.2.1.7
	DC Power to Antenna Lightning Criteria (Type 8a Ports)
	R4-26 [253]
	ER

	
	DC Power to top of Antenna
	R4-27 [240]
	ER

	4.6.3.1
	Second Level Lightning for Telecommunication Ports
	-
	-

	
	   Type 1, 3, and 5 Ports
	R4-28 [29]
	ER

	
	  Circuit Pack Labeling
	R4-29 [241]
	ER

	4.6.3.2
	Second Level Lightning for AC Power Ports (Type 7 Ports)
	-
	-

	
	Conformance Criteria
	R4-30 [33]
	ER

	4.6.4
	Power Fault Requirements
	-
	-

	4.6.4.1
	First-Level Power Fault/Induction
	
	

	
	 Damage and Operating Requirements
	R4-32 [35]
	ER

	
	 Ports with Secondary Protection
	R4-33 [172]
	ER

	
	 Ports with Secondary Protection with Self-Resettable Current Limiting
	R4-34 [173]
	ER

	4.6.4.2
	Second-Level Power Fault Requirements
	-
	-

	
	  Type 3a/5a, 3b/5b, 4 and 4a Ports
	R4-35 [40]
	ER

	
	  Warning Requirement
	R4-36 [41]
	ER

	
	  Type 1, 3, 5 Ports 
	R4-37 [36]
	ER

	
	  Ports with Secondary Protector
	R4-38 [174]
	ER

	
	Ports with Current Limiting Device
	R4-39 [175]
	ER

	4.7
	Criteria for Equipment with Integrated Primary Protection (EIPP)
	R4-40 [182]
	ER

	4.7.1
	Equipment Classification
	-
	-

	
	  EIPP Installation Documentation
	R4-41 [183]
	ER

	
	  EIPP Equipment Classification
	R4-42 [184]
	ER

	4.7.2
	Protector Requirements
	-
	-

	
	Listing Requirement for Primary Protector Units
	R4-43 [185]
	ER

	
	    EIPP Listing Requirement
	R4-44 [186]
	ER

	
	  EIPP Installation Provisions
	R4-45 [187]
	ER

	
	  EIPP Labeling
	R4-46 [188]
	ER

	
	  Appropriate Assembly
	R4-47 [189]
	ER

	
	  Protector Characteristics
	R4-48 [190]
	ER

	4.7.3
	Lightning Surge and Power Fault Tests for Protected Circuits
	R4-49 [191]
	ER

	4.7.4.1
	Fusing Coordination for Circuits that Contain Components or Circuitry that Act as OSP Fuse Links
	R4-50 [193]
	ER

	4.7.4.1.1
	Enclosure Suitable for Fusing
	
	

	
	Metal EIP Enclosure Thickness
	R4-51 [194]
	ER

	
	Polymetric EIPP Enclosures
	R4-52 [195]
	ER

	
	Vents and Openings
	R4-53 [196]
	ER

	4.7.4.2
	Fusing Coordination for Circuits Not Containing Components or Circuitry That Act as OSP Fuse Links
	R4-54 [199]
	ER

	4.7.5
	Dielectric Withstand
	R4-55 [200]
	ER

	4.7.6
	EIPP Cable Requirements
	
	

	
	Appropriate for Application
	R4-56 [201]
	ER

	
	Shielding
	R4-57 [202]
	ER

	4.7.7
	AC Power Fault Immunity – Unprotected Circuits
	R4-58 [203]
	ER

	4.7.8
	Lightning Surge Tests – Unprotected Circuits
	R4-59 [204]
	ER

	4.7.8.1
	Lightning Surge Tests for Severe Climatic Conditions – Unprotected Units
	
	

	
	First –Level Surge Tests
	CR4-60 [205]
	ER

	
	Fire Hazard
	CR4-61 [206]
	ER

	5
	Steady-State Power Induction
	-
	-

	5.2.3.2
	Analog Loop Criteria
	-
	-

	
	Performance Criteria
	-
	-

	
	  Requirement
	R5-1 [42]
	ER

	
	  Conditional Requirement
	CR5-2 [43]
	ER

	
	Noise Performance for Voice band Circuits Requirement
	R5-3 [44]
	ER

	
	  Conditional Requirement
	CR5-4 [45]
	ER

	5.2.3.3
	Digital Loop Testing
	
	

	
	BER Performance Measurement, 50 Vrms
	R5-5 [46]
	ER

	
	BER Performance Measurement, 80 Vrms
	CR5-6 [243]
	ER

	5.2.3.4
	Line/Span Powering Loop Testing
	
	

	
	Power Circuity Operation, 50 Vrms
	R5-7 [244]
	ER

	
	Power Circuity Operation, 80 Vrms
	CR5-8 [245]
	ER

	6
	DC Potential Difference
	R6-1 [53]
	ER

	7
	Electrical Safety Criteria
	-
	-

	7.2
	Listing Requirements
	-
	-

	
	  AC Powered Network Equipment
	R7-1 [22]
	ER

	
	  Convenience Receptacles
	R7-2 [23]
	ER

	
	  Customer Premises Equipment
	R7-3 [24]
	ER

	
	Class A2 or A3 Line Powering 
	R7-4 [254]
	ER

	7.3
	Classification of Voltages
	R7-5 [143]
	ER

	7.3.1
	Continuous Voltage and Current Limits
	
	

	
	  Continuous Source
	R7-6 [115]
	ER

	
	  Ground Fault or Voltage Shutdown
	R7-7 [144]
	ER

	7.4
	Continuous Source Requirements
	-
	-

	7.4.1
	Class A1 Voltage Accessibility Requirements
	R7-8 [54]
	ER

	7.4.2
	Class A2 Voltage Accessibility Requirements
	R7-9 [55]
	ER

	7.4.3
	Class A3 Voltage Accessibility Requirements
	-
	-

	
	  Inaccessible
	R7-10 [56]
	ER

	
	  Insulation, Baffling, or Location
	R7-11 [57]
	ER

	
	  Labeled
	R7-12 [58]
	ER

	7.4.4
	Class AB Voltage Accessibility Requirements
	
	

	
	  OSP
	R7-12 [59]
	ER

	
	  Inaccessible
	R7-13 [60]
	ER

	
	  No Bare-Handed Contact
	R7-14 [61]
	ER

	
	  Labeled
	R7-15 [62]
	ER

	7.4.5
	Class B Voltage Accessibility Requirements
	R7-17 [63]
	ER

	7.5
	Duration-Limited Source Requirements
	-
	-

	7.5.1
	Interrupted/Tripped Sources
	
	

	
	  > 300V Peak-to-Peak
	R7-18 [64]
	ER

	
	  No Exceed Class A2 Voltage Limit
	R7-19 [65]
	ER

	
	  Series Current-Sensitive Tripping Device
	R7-20 [66]
	ER

	
	  NRTL Data
	R7-21 [145]
	ER

	7.5.2
	Transient Sources
	R7-22 [67]
	ER

	7.6
	Power Limitation Requirement
	R7-23 [68]
	ER

	7.7
	Leakage Currents from Exposed Surfaces
	-
	-

	7.7.2.1
	Leakage Current Requirements for Large Area Contact
	R7-24 [69]
	ER

	7.7.2.2
	Leakage Current Requirements for Small Area Contact
	R7-25 [70]
	ER

	7.7.2.3
	Leakage Current Between Surfaces of Equipment
	R7-26 [71]
	ER

	7.8
	Laser Safety and Labeling Criteria
	R7-27 [246]
	ER

	8
	Corrosion
	-
	-

	8.1
	Polarity of DC Voltages Applied to OSP Cabling
	O8-1 [72]
	ER

	8.2
	Magnitude of DC Voltages Applied to OSP Cabling
	O8-2 [73]
	ER

	9
	Bonding and Grounding
	-
	-

	9.2
	General Requirements Principles
	-
	-

	
	  Bonding Path Provided
	R9-1 [75]
	ER

	9.3
	Equipment Grounding Systems
	R9-2 [76]
	ER

	9.3.1
	Common Bonding Network (CBN)
	R9-3 [116]
	ER

	9.4
	AC Equipment Grounding
	R9-4 [77]
	ER

	9.5
	Communication Equipment Grounding
	R9-5 [213]
	ER

	9.5.1
	Network Telecommunications Facilities
	R9-6 [78]
	ER

	9.5.2
	Locations Where the NEC Applies
	R9-7 [146]
	ER

	9.5.3
	Outside Plant
	R9-8 [147]
	ER

	9.6
	Equipment Unit Bonding and Grounding
	R9-9 [79]
	ER

	9.7
	Provisions for Unit Assembly Bonding and Grounding
	R9-10[148]
	ER

	9.7.1
	Connectors and Connection Methods for Equipment Unit Assemblies
	R9-11 [149]
	ER

	9.7.2
	Bonding of Circuit Packs
	R9-12 [150]
	ER

	9.8
	DC Power System Grounding
	-
	ER

	9.8.1
	Centralized Power Sources
	R9-13 [80]
	ER

	9.8.2
	Embedded Power Sources
	R9-14 [81]
	ER

	9.8.3
	Bonding of Battery Return (BR) Input Terminals
	-
	

	
	  Documentation
	R9-15 [151]
	ER

	
	Equipment in a DC-I Configuration
	R9-16 [255]
	ER

	
	  Conductor Ampacity
	R9-17 [152]
	ER

	9.9.1
	Bonding and Grounding Conductors
	R9-18[82]
	ER

	9.9.2
	Connections
	-
	

	
	  Suitable Materials
	R9-19 [83]
	ER

	
	  Bare Conductors
	R9-20 [84]
	ER

	
	  Multiple Connectors
	R9-21 [85]
	ER

	
	  Unplated Connectors
	R9-22 [86]
	ER

	
	  Listed Fastening Hardware
	R9-23 [87]
	ER

	
	  Nonconductive Coatings
	R9-24 [88]
	ER

	9.9.3
	Connectors
	
	-

	
	  Listed
	R9-25 [89]
	ER

	
	  Grounding and Bonding Conductors
	R9-26 [90]
	ER

	
	  Conductor Termination
	R9-27 [91]
	ER

	9.10.1
	DC Power Sources
	R9-28 [92]
	ER

	9.10.2
	AC Power Sources
	R9-29 [93]
	ER

	9.12
	Compatibility of Former IBN Equipment with CBN Currents
	-
	

	9.12.1.7
	Test Environment
	CR9-30 [117]
	ER

	9.12.2
	Identification of Test Points
	R9-31 [118]
	ER

	9.12.3
	DC Fault Test
	CR9-32 [119]
	ER

	9.12.4
	Frame EFT Test
	CR9-33 [121]
	ER

	9.12.5
	Frame Surge Test
	-
	

	
	3000A, 8/20-µs current surge
	CR9-34 [122]
	ER

	
	5000A, 8/20-µs current surge
	CO9-35 [123]
	ER

	9.12.6
	AC Fault Test
	CR9-36 [120]
	ER

	9.13
	Grounding connector for Equipment With Integrated Primary Protection
	-
	

	
	  Common Bonding Point
	R9-37 [214]
	ER

	
	  60-Hz, 1500A for 6 Seconds
	R9-38 [215]
	ER

	9.13.1
	Grounding Conductors in the EIPP
	-
	

	
	  Unless Fusing on the EUT Board
	R9-39 [216]
	ER

	
	  If Fusing on the EUT Board
	R9-40 [217]
	ER

	10
	Criteria for DC Power Port of Telecommunications Load Equipment
	-
	

	10.1
	Input DC Voltage
	R10-1 [247]
	ER

	10.2
	Minimum Operating Voltage
	R10-2 [19]
	ER

	10.3
	Overvoltage (Steady State)
	R10-3[249]
	ER

	10.4
	 Overvoltage Transient
	R10-4 [222]
	ER

	10.5
	 Protective Device Operation Transient
	R10-5 [223]
	ER

	10.6
	Noise Returned by the Network Equipment (Noise Emission)
	R10-6 [249]
	ER

	10.7
	Power Input Noise Immunity
	R10-7 [228]
	ER

	10.8
	Markings and Documentation
	R10-8[250]
	ER


4. APPENDIX B.








Test Report Certification

A completed copy of this certification must be attached to each test report.  The carrier will not accept test reports without accurate and complete certifications.  Please direct any questions to the carrier’s NEBS compliance contact.

	Report Number
	Name of Test Lab
	Address of Test Lab
	Report Date

	
	
	
	


	Test Description
	Name of Test Lab
	Address of Test Lab
	Date of test

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


Independent Test Laboratory Director:  I hereby certify that the NEBS testing described in the indicated report was performed according to the NEBS requirements listed in the Telecommunications Carrier NEBS Checklist and the applicable ANSI and Telcordia NEBS Generic Requirements.  I also certify that the testing was performed at the laboratory locations, dates and times listed above.  

	Signature, Title, Organization 
	Date

	
	


Manufacturer’s Test Laboratory Director:  I hereby certify that the NEBS testing described in the indicated report has been performed according to the NEBS requirements listed in the Telecommunications Carrier NEBS Checklist and the applicable ANSI and Telcordia NEBS Generic Requirements.  I also certify that the testing was performed at the laboratory locations, dates and times listed above.
	Signature, Title, Organization 
	Date

	
	


5. APPENDIX C. NEBS 







Compliance Checklist

(All applicable information must be provided to avoid evaluation delays.  

Please direct any questions of applicability to the carrier’s NEBS compliance contact.)

A.  GENERAL INFORMATION   (Required for CLEC & Carrier Applications.)
	1Date:
	
	(Initial)

	
	Date:
	
	(Revised, All changes shall be clearly highlighted or identified)


	2Supplier Name:


	

	3Supplier  Contact:


	
	4Phone #:
	

	5Supplier e-mail address:
	
	6FAX #:
	

	7Equipment type/name:


	

	8System/Model Number:
	

	9Detailed Configuration Information:
	

	

	

	


	If equipment has optional configurations, modules, plug-in cards or circuit packs, a complete listing of modules/units must be included – please clearly show unit names, model numbers and plug-in card relationships. Attach lists and sketches of tested hardware units showing specific module locations, to this checklist.  Complete the table below (items 15, 16 and 17) as required. Duplicate or repeat the table or lines as necessary.


	10Shelf description:

	Manufacturer:
	Model Name/Number:
	Part Number:

	
	
	

	11Plug-in card or module descriptions for above shelf (List only one of each type :)

	Model/Name:
	Part Number: 

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	
	

	12Remarks for above shelf or plug-ins:
	

	

	

	


	13Carrier use ______ (Yes or ZN   NO

	No)
	
	14Collocator use (Name):


	_______________________________________________

	
	
	
	
	

	15Project/Application description:  Specify Function, Customer Premises, Host/Remote, COT/RT, number of sites, specific States/Cities, Carrier wide, etc.:



	

	

	


B.  POWER REQUIREMENTS   (Required for CLEC & Carrier Applications.  All items must be answered – Do not change any measurement units)
	1-48v DC
 (Carrier Preferred):



	Yes
	
	No
	
	Amps


	
	
	Watts
	

	2Alternate/Additional Requirements:
	
	Amps


	
	
	Watts
	

	3Peripheral Equipment Requirements:
	
	Amps
	
	
	Watts
	

	4Power Drain: 
	
	List 1
	
	
	List 2
	

	5Return Current Architecture Equipment Requirements:
	
	DC-I
	
	
	DC-C
	

	6Is AC power mandatory for any system component:


	
	
	
	Yes
	
	
	No
	
	

	7Is this power information representative of a specific, typical or maximum configuration?


	
	

	8List equipment voltage classification(s) per GR-1089, Section 7.3:

	Class:
	
	

	9Comments/Describe:
	

	


C.  GROUNDING REQUIREMENTS    (Required for CLEC & Carrier Applications.  Refer to GR-295-CORE; this is not the same as UL 1950.  All items must be answered)
	1 Does this equipment conform to the Integrated Ground Plane requirements in GR-1089 Section 9?
	
	Yes
	
	
	No
	
	

	2Is this equipment compatible with the GR-295 for Isolated Ground Plane?
	
	Yes
	
	
	No
	
	

	3Is internal logic ground isolated from chassis/framework ground?
	
	Yes
	
	
	No
	
	

	4Is signal ground, external interface, isolated from chassis/framework ground?
	
	Yes
	
	
	No
	
	

	5Is chassis/framework used as a current carrying conductor?
	
	Yes
	
	
	No
	
	

	6Comments/Describe:
	

	


D.  PHYSICAL SIZE/MOUNTING REQUIREMENTS    (Required for CLEC & Carrier Applications.  All items must be answered – Do not change any measurement units)
	1 Is equipment a circuit pack, shelf, frame, rack, cabinet or multiple frames? Explain if required.


	
	

	

	

	2 Does equipment mount on a relay rack or cabinet included as part of system?
	
	Yes
	
	
	No
	
	

	3 Does cabinet or equipment unit/mounting have doors or removable covers on front?
	
	Yes
	
	
	No
	
	

	4 Does cabinet or equipment unit/mounting have doors or removable covers on rear?
	
	Yes
	
	
	No
	
	

	5 Is access to rear of relay rack/cabinet required for maintenance?
	
	Yes
	
	
	No
	
	

	6 Is metallic cabling terminated on the rear of equipment?
	
	Yes
	
	
	No
	
	

	7 Are fiber cables and test access points terminated on the front of equipment?
	
	Yes
	
	
	No
	
	

	8 Does the equipment include cable guards/strain relief?
	
	Yes
	
	
	No
	
	

	9 Does the equipment automatically reduce power to open fiber ports?
	
	Yes
	
	
	No
	
	

	10 Do fiber ports point downward?
	
	Yes
	
	
	No
	
	

	11Is equipment installed exclusively indoors in a CO, CEV, HUT, or customers’ Premises?
	
	Yes
	
	
	No
	
	

	12 Is Equipment installed exclusively outdoors in a metal enclosure?
	
	Yes
	
	
	No
	
	

	13 Equipment dimensions measured in normal mounting configuration.
	Height
	
	
	Inches

	
	Width
	
	
	Inches

	
	Depth
	
	
	Inches

	14 Minimum aisle clearance required for fully open door ‘clear swing’ – front.
	
	
	
	Inches

	15 Minimum aisle clearance required for fully open door ‘clear swing’ – rear.
	
	
	
	Inches

	16 Equipment total weight.
	
	
	
	Lbs.

	17 Comments:
	

	


E.  HEAT RELEASE DATA (Required for CLEC & Carrier Applications.)
	1 Is equipment forced air-cooled by its own fan unit?
	
	Yes
	
	_____
	No
	
	______

	2 Does the equipment use replaceable air filters? 
	
	Yes
	
	
	No
	
	

	3 Does heat release vary with traffic load?
	
	Yes
	
	
	No
	
	

	4 Describe product airflow, intake to exhaust.  (i.e. bottom front to top rear)
	

	5 Is heat release calculated for a specified traffic level?
	
	Yes
	
	
	No
	
	

	6 If yes, specify the traffic level used in the calculated heat release.
	
	
	
	CCS

	7 Maximum Aisle Facing Surface Temperature (GR‑63: R4‑33 [159]).
	
	
	
	oF


	List each active component in system:
	No. Units to be Used in System1
	Heat Dissipation per Unit/Traffic %2
	Heat Dissipation per total sub-system3

	Description/Card Number
	Part Number
	A: Max

Possible:
	B: This System:
	C: Max % Traffic :
	D: This System:
	Watts Max

A x C
	Watts this          System B x D

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	

	Total Watts for System:
	
	


Notes:

1 Max Poss:  The maximum number of units of this component that can be used in the system as designed

This System:  The maximum number of units of this component per planned deployment

2     Max %:  Heat dissipation for a unit in watts, when operating at maximum capacity

This System:  Heat dissipation for a unit in watts, when operating at maximum capacity expected for deployment

3
Watts Max:  Maximum number of units times maximum heat dissipation per unit

Watts This System:  Maximum number of units for this system times estimated heat dissipation per unit under maximum capacity when deployed 

F.  ALARM AND PERFORMANCE MONITORING INTERFACE
	1 Do all fuse alarms provide audible, visual, local, and remote reporting?
	
	Yes
	
	
	No
	
	

	2 Does equipment include a provision for connection to local/remote external alarms and/or performance monitoring systems?
	
	Yes
	
	
	No
	
	

	3 Can alarms be transmitted to remote locations?
	
	Yes
	
	
	No
	
	

	4 Can alarms be retired from remote locations?
	
	Yes
	
	
	No
	
	

	5 Can alarms be ‘obscured’ by other (e.g., lower level) alarms?
	
	Yes
	
	
	No
	
	

	6 Does equipment interface require proprietary Operational Support Systems?
	
	Yes
	
	
	No
	
	

	7 Identify/Describe proprietary Operational Support Systems: 
	
	

	

	8 Specify supported performance-monitoring interfaces. [Example: TNM/NFM, SNMP, TL1, CORBA, others?]

	

	

	9 Additional Comments or Descriptions: 
	
	

	

	


G. GR-78 PHYSICAL DESIGN REQUIREMENTS   (Required for Carrier Applications, All items must be answered.  See Section 3.8.)
	GR-78 Section
	Element Requirement Description
	Compliant
	Exceptions and Remarks

	3
	Materials and Finishes Requirements
	
	
	
	
	
	

	3.1
	General: R3-4 [41] –R3-5 [42]
	Yes
	
	No
	
	
	

	3.2.2
	Fire Risk Analysis: R3-10 [47], R3-11 [48] (Component Rating UL94, V-0 or V1), R3-12 [49]
	Yes
	
	No
	
	
	

	3.2.3&3.2.4
	Fluxes: R3-13 [50] / Silver - CR3-15 [52]
	Yes
	
	No
	
	
	

	3.2.5
	Silicones: R3-16 [53]
	Yes
	
	No
	
	
	

	3.3
	Finishes: R3-17 [54]-R3-24 [60] (min 2% lead)
	Yes
	
	No
	
	
	

	4
	Separable Connector Requirements
	
	
	
	
	
	

	4.1.1
	Selection Considerations: R4-1 [61] through O4-21 [80]
	Yes
	
	No
	
	
	

	4.1.2
	Lubrication (Contacts): R4-32 [95] through R4-40 [100]
	Yes
	
	No
	
	
	

	4.1.3
	Connector Durability: R4-41 [865] -R4-42 [866]
	Yes
	
	No
	
	
	

	4.2
	Two-Part and PWB Edge Card Connectors
	
	
	
	
	
	

	4.2.1
	Design R60 [116]
	Yes
	
	No
	
	
	

	4.2.2
	Polarization R4-62 [118] – R4-64 [120]
	
	
	
	
	
	

	4.2.3
	Insertion and Removal Forces R4-65 [121] – R4-68 [123]
	Yes
	
	No
	
	
	

	4.3


	Insulation Displacement Connectors (IDCs)      R4-72 [129] -R4-74 [131]
	Yes
	
	No
	
	
	

	5
	Wire and Cable Requirements
	
	
	
	
	
	

	5.1
	Metallic Wire and Cable  R5-1 [138]
	Yes
	
	No
	
	
	

	5.1.4
	Materials -  R5-4 [141] – R5-8 [145]
	Yes
	
	No
	
	
	

	5.1.5
	Performance -   R5-11 [148] – R5-18 [868]
	Yes
	
	No
	
	
	

	5.1.6
	Wire and Cable Preparation for Equipment Assemblies -   R5-23 [159] – R5-27 [163]
	Yes
	
	No
	
	
	

	5.1.7
	Cable and Wire Termination -   R5-28 [164]  – R5-33 [169]
	Yes
	
	No
	
	
	

	5.2
	Optical Fiber and Optical Fiber Cables
	
	
	
	
	
	

	6.
	Printed Wiring Board Requirements
	
	
	
	
	
	

	6.1
	General -  R6-1 [171]
	Yes
	
	No
	
	
	

	6.1.1
	Materials
	
	
	
	
	
	

	6.1.1.1
	Laminates – R6-2 [172] – R6-3 [173]
	Yes
	
	No
	
	
	

	6.1.1.2
	Solder Mask – R6-4 [174] – R6-5 [175]
	Yes
	
	No
	
	
	

	6.1.1.3
	Legend and Marking Inks -  R6-6 [176]
	Yes
	
	No
	
	
	

	6.1.1.4
	Repair Polymers  - R6-7 [177]
	Yes
	
	No
	
	
	

	6.1.1.5
	Conductor Materials and Finishes -  R6-8 [178] – R6-12 [872]
	Yes
	
	No
	
	
	

	6.1.2
	Design
	
	
	
	
	
	

	6.1.2.1
	Dimensioning – R6-13 [179] – R6-14 [180]
	Yes
	
	No
	
	
	

	6.1.2.2
	PWB Contact Fingers – O6-15 [181] – CR6-19 [185]
	Yes
	
	No
	
	
	

	6.1.2.3
	Interlayer Connections  - R6-20 [186] – R6-24 [874]
	Yes
	
	No
	
	
	

	6.1.2.4
	Warpage – R6-25 [189] – IP6-26 [190]
	Yes
	
	No
	
	
	

	6.1.2.5
	Protective Coatings – R6-27 [191]
	Yes
	
	No
	
	
	

	6.1.2.6
	Resistance to Airborne Contaminants – R6-28 [192]
	Yes
	
	No
	
	
	

	6.1.3
	Manufacturing
	
	
	
	
	
	

	6.1.3.1
	General – R6-29 [193] – R6-31 [195]
	Yes
	
	No
	
	
	

	6.1.3.2
	Conductor Widths and Spacing – R6-32 [195] – R6-38 [202]
	Yes
	
	No
	
	
	

	6.1.3.3
	Conductor Adhesion – R6-39 [203]
	Yes
	
	No
	
	
	

	6.1.3.4
	Plated Through Holes (PTHs) CR6-41 [205] – R6-53 [215]
	Yes
	
	No
	
	
	

	6.1.3.5
	Conductor Finishes – R6-54 [216] – R6-56 [218]
	Yes
	
	No
	
	
	

	6.1.3.6
	Solderability – R6-57 [219]
	Yes
	
	No
	
	
	

	6.1.3.7
	Solder Masks – R6-58 [220] – R6-70 [232]
	Yes
	
	No
	
	
	

	6.1.3.8
	PWB Contact Fingers – R5-73 [235] – R6-87 [247]
	Yes
	
	No
	
	
	

	6.1.3.9
	Insulation Resistance Testing
	
	
	
	
	
	

	6.1.3.9.1
	Surface Insulation Resistance  - R6-88 [248] – R6-93 [253]
	Yes
	
	No
	
	
	

	6.1.3.10
	Solvent Extract Conductivity Testing – R6-95 [255] -R6-102 [262]
	Yes
	
	No
	
	
	

	6.1.3.11
	Mechanical Damage – R6-105 [265] – R6-118 [278]
	Yes
	
	No
	
	
	

	6.1.3.12
	Laminate and Processing Defects – R6-120 [280] – R6-125 [285]
	Yes
	
	No
	
	
	

	6.1.3.13
	Electrical – R6-126 [286] – R6-131 [291]
	Yes
	
	No
	
	
	

	6.1.3.14
	Repairs – R6-132 [292] – R6-143 [303]
	Yes
	
	No
	
	
	

	6.1.3.15
	Modifications – General  - CR6-144 [304] – R6-148 [308]
	Yes
	
	No
	
	
	

	6.1.3.16
	Modifications – Subtractive – CR6-149 [309] – R6-157 [317]
	Yes
	
	No
	
	
	

	6.1.3.17
	Modifications – Additive – R6-158 [318] – R6-174 [334]
	Yes
	
	No
	
	
	

	6.2
	Multi-layer PWBs - General Requirement
	
	
	
	
	
	

	6.2.1.1
	Dimensioning: R6-175 [335] through R6-185 [340]
	Yes
	
	No
	
	
	

	6.2.1.2
	Interlayer Connections:  R6-186 [341] – R6-189 [343]
	Yes
	
	No
	
	
	

	6.2.1.3
	Construction: R6-191[345] through R6-196 [350]
	Yes
	
	No
	
	
	

	6.2.2
	Manufacturing
	
	
	
	
	
	

	6.2.2.1
	Conductor Widths and Spacings
	
	
	
	
	
	

	6.2.2.2
	Plated Through Holes:  R6-199 [353] – R6-204 [358]
	Yes
	
	No
	
	
	

	6.2.2.3
	Insulation Resistance Testing Inner Signal Layers: R6-205 [359] – R6-207 [361]
	Yes
	
	No
	
	
	

	6.2.2.4
	Insulation Resistance Testing– Interlayer:  R6-208 [362]
	Yes
	
	No
	
	
	

	6.2.2.5
	SEC Testing: R6-209 [363] – R6-212 [366]
	Yes
	
	No
	
	
	

	6.2.2.6
	Laminate and Processing Defects: R6-213 [367] -R6-214 [368]
	Yes
	
	No
	
	
	

	6.2.2.7
	Electrical Requirements: R6-215 [369] – R6-218 [372]
	Yes
	
	No
	
	
	

	6.2.2.8
	Repairs – Inner Layers Before Lamination:        R6-219 [373] -R6-223 [377]
	Yes
	
	No
	
	
	

	6.2.2.9
	Repairs – Finished Multilayer PWBs:   R6-224 [378] -R6-225 [379]
	Yes
	
	No
	
	
	

	6.2.2.10
	Modifications – Inner Layers Before Lamination: R6-226 [380] -R6-228 [382]
	Yes
	
	No
	
	
	

	6.2.2.11
	Modifications – Completed Multilayer PWBs:   R6-229 [383]
	Yes
	
	No
	
	
	

	6.3
	PWBs for Surface Mounting
	
	
	
	
	
	

	6.3.1.1
	Materials: laminates - R6-230 [384]
	Yes
	
	No
	
	
	

	6.3.1.2
	Materials: solder masks - R6-231 [385]
	Yes
	
	No
	
	
	

	6.3.1.3
	Component mounting pads: R6-232 [386] through CR6-237 [391]
	Yes
	
	No
	
	
	

	6.3.1.4
	Design – Solder Masks IP6-238 [392]
	Yes
	
	No
	
	
	

	6.3.1.5
	PWBs for Adhesive and Wave solder Soldering Processes – Conductor Finish  IP6-239 [393]
	Yes
	
	No
	
	
	

	6.3.1.6 
	PWBs for Adhesive and Wave solder Soldering Processes – Component Mounting Pads 06-240 [394] – R6-244 [397]
	Yes
	
	No
	
	
	

	6.3.1.7
	PWBs for Reflow Surface-Mount Soldering Processes – Conductor Finish R6-245 [398]
	Yes
	
	No
	
	
	

	6.3.1.8
	PWBs for Reflow Surface-Mount Soldering Processes – Component Mounting Pads R6-246 [399] -O6-251 [404]
	Yes
	
	No
	
	
	

	6.4
	PWBs for Backpanels
	
	
	
	
	
	

	6.4.1
	Design
	
	
	
	
	
	

	6.4.1.1
	Dimensioning CR6-252 [405] – CR6-253 [406]
	Yes
	
	No
	
	
	

	6.4.1.2
	Method of Manufacture R6-254 [407]
	Yes
	
	No
	
	
	

	6.4.2
	Manufacturing
	
	
	
	
	
	

	6.4.2.1
	Drilling   O6-258 [411]
	Yes
	
	No
	
	
	

	6.4.2.2
	Plated Through Holes (PTHs) R6-259 [412] -R6-261 [414]
	Yes
	
	No
	
	
	

	6.5
	Encapsulated Discrete Wire (EDW) Interconnection Boards – Basic Construction R6-262 [415] -R6-265 [418]
	Yes
	
	No
	
	
	

	7
	PWB Assembly Requirements
	
	
	
	
	
	

	7.1.1.1
	Conformal Coating - R7-1 [419] & R7-2 [420]
	Yes
	
	No
	
	
	

	7.1.1.2
	Fluxes R7-3 [421] – R7-4 [422]
	Yes
	
	No
	
	
	

	7.1.1.3
	Solders and Solder Pastes  07-5 [884] – CR7-9 [888]
	Yes
	
	No
	
	
	

	7.1.2.
	Assembly Design
	
	
	
	
	
	

	7.1.2.1
	General O7-10 [423] – R7-22 [435]
	Yes
	
	No
	
	
	

	7.1.2.2
	Components  R7-23 [436] – R7-33 [445]
	Yes
	
	No
	
	
	

	7.1.2.3
	Layout – General  R7-35 [448] – R7-38 653] 
	Yes
	
	No
	
	
	

	7.1.2.4
	Layout: Thermal Considerations R7-39 [451] – R7-42 [454]
	Yes
	
	No
	
	
	

	7.1.2.5
	Layout – Clearances  R7-43 [455] – R7-52 [464]
	Yes
	
	No
	
	
	

	7.1.2.6
	Layout – Lead Forms  R7-54 [466] – R7-58 [470]
	Yes
	
	No
	
	
	

	7.1.2.7
	Separable Connections – See Section 4
	
	
	
	
	
	

	7.1.2.8
	Conformal Coatings  R7-59 [471]
	Yes
	
	No
	
	
	

	7.1.3
	Manufacturing 
	
	
	
	
	
	

	7.1.3.1
	General R7-60 [487] – R7-86 [498]
	Yes
	
	No
	
	
	

	7.1.3.2
	Clearances R7-87 [499] – R7-89 [501]
	Yes
	
	No
	
	
	

	7.1.3.3
	Solderability R7-91 [503]
	Yes
	
	No
	
	
	

	7.1.3.3.4
	Soldering R7-92 [509] through R7-102 [513]
	Yes
	
	No
	
	
	

	7.1.3.5
	Bow and Twist R7-103 [514]
	Yes
	
	No
	
	
	

	7.1.3.6
	Solder masks: R7-104 [515]
	Yes
	
	No
	
	
	

	7.1.3.7
	Conformal coatings: R7-107 [518]
	Yes
	
	No
	
	
	

	7.1.3.8
	Insulation Resistance Testing O7-108 [521] – O7-111 [522]
	Yes
	
	No
	
	
	

	7.1.3.9
	SEC Testing  O7-114 [526] – 07-115 [525]
	Yes
	
	No
	
	
	

	7.1.3.10
	Lubrication CR7-116 [890] – CR7-117 [891]
	Yes
	
	No
	
	
	

	7.1.3.11
	Mechanical Damage and Defects R7-118 [527]
	Yes
	
	No
	
	
	

	7.1.3.12
	Repair of PWB Assemblies – General R7-122 [531] – R7-125 [534]
	Yes
	
	No
	
	
	

	7.1.3.13
	Repair of PWB Assemblies – Component Removal and Replacement R7-126 [892] – R7-140 [544]
	Yes
	
	No
	
	
	

	7.1.3.14
	Repair of PWB Assemblies – PWB Repairs R7-141 [545] – R7-143 [547]
	Yes
	
	No
	
	
	

	7.1.3.15
	Modifications to PWB Assemblies – General    R7-144 [548] - R7-145 [549]
	Yes
	
	No
	
	
	

	7.1.3.16
	Modifications to PWB Assemblies – Wiring Design  R7-147 [551] – R7-151 [555]
	Yes
	
	No
	
	
	

	7.1.3.17
	Modifications to PWB Assemblies – Wire Routing  R7-152 [556] – R7-156 [560]
	Yes
	
	No
	
	
	

	7.1.3.19
	Modifications to PWB Assemblies – Soldering of Modification Wires  CR7-159 [563] – R7-163 [567]
	Yes
	
	No
	
	
	

	7.1.3.20
	Modifications to PWB Assemblies – Securing of Modification Wires  R7-166 [570] – R7-178 [582]
	Yes
	
	No
	
	
	

	7.1.3.22
	Modifications to PWB Assemblies – Components R7-185 [589] – CR7-191 [595]
	Yes
	
	No
	
	
	

	7.2
	PWB Assemblies – Through-Hole Mounted Components
	
	
	
	
	
	

	7.2.1
	Assembly Design  R7-192 [596]
	Yes
	
	No
	
	
	

	7.2.2
	Manufacturing
	
	
	
	
	
	

	7.2.2.1
	Soldering – PTH Solder Joints  O7-197 [601] – R7-200 [604]
	Yes
	
	No
	
	
	

	7.2.2.3
	Compliant Pin  R7-205 [71]
	Yes
	
	No
	
	
	

	7.3
	PWB Assemblies – Surface Mounted Components (SMCs)
	
	
	
	
	
	

	7.3.1.1
	Solder Pastes – Incoming Material Controls      R7-210 [613]
	Yes
	
	No
	
	
	

	7.3.1.2
	Solder Pastes – In-Process Controls R7-211 [614] -R7-217 [620]
	Yes
	
	No
	
	
	

	7.3.1.4
	Adhesives  R7-218 [621] – R7-220 [623]
	Yes
	
	No
	
	
	

	7.3.2
	Assembly Design
	
	
	
	
	
	

	7.3.2.1
	General  R7-221 [624]
	Yes
	
	No
	
	
	

	7.3.2.2
	Components  IP7-222 [625] – CR7-223 [626]
	Yes
	
	No
	
	
	

	7.3.2.3
	Thermal Considerations  R7-224 [627]
	Yes
	
	No
	
	
	

	7.3.2.4
	Lead Forms  R7-225 [628]
	Yes
	
	No
	
	
	

	7.3.2.5
	Termination Metallizations  R7-226 [629]
	Yes
	
	No
	
	
	

	7.3.3
	Reliability  R7-227 [630] – R7-230 [633]
	Yes
	
	No
	
	
	

	7.3.4
	Manufacturing
	
	
	
	
	
	

	7.3.4.1
	Soldering – General  R7-231 [634]  – R7-232 [635]
	Yes
	
	No
	
	
	

	7.3.4.2
	Soldering – Reflow Processes  R7-233 [636] – IP7-234 [637]
	Yes
	
	No
	
	
	

	7.3.4.3
	Soldering – Wave soldering Processes  R7-235 [638] – R7-238 [897]
	Yes
	
	No
	
	
	

	7.3.4.5
	Electrical Requirements R7-239 [641]
	Yes
	
	No
	
	
	

	7.3.4.6
	Repairs  R7-240 [642]
	Yes
	
	No
	
	
	

	7.3.4.7
	Modifications  R7-243 [645]
	Yes
	
	No
	
	
	

	7.3.4.8
	Ball Grid Array (BGA) Assembly  R7-245 [647] – R7-253 [656]
	Yes
	
	No
	
	
	

	7.4
	Backpanel PWB Assemblies  R7-254 [659]
	Yes
	
	No
	
	
	

	7.4.1
	Assembly Design
	
	
	
	
	
	

	7.4.1.1
	Terminals/Pins  R7-255 [657]  – O7-257 [898]
	Yes
	
	No
	
	
	

	7.4.1.2
	Dimensioning  R7-258 [660]
	Yes
	
	No
	
	
	

	7.4.2.1
	Manufacturing -  Dimensions  R7-259 [661] – R7-261 [663]
	Yes
	
	No
	
	
	

	7.4.2.2
	Electrical Requirements   O7-262 [664]
	Yes
	
	No
	
	
	

	7.4.2.3
	Plated Through Hole (PTH)  Deformation/Damage  R7-265 [667]
	Yes
	
	No
	
	
	

	8.
	Equipment Sub-Assembly and Assembly Requirements
	
	
	
	
	
	

	8.1
	General
	
	
	
	
	
	

	8.1.2
	Sub-Assemblies and Assemblies  R8-1 [668] – R8-2 [669]
	Yes
	
	No
	
	
	

	8.1.3
	Design  R8-11 [678] – R8-30 [696]
	Yes
	
	No
	
	
	

	8.2
	Manufacturing
	
	
	
	
	
	

	8.2.1
	Connections
	
	
	
	
	
	

	8.2.1.1
	General  R8-31 [697] – R8-33 [699]
	Yes
	
	No
	
	
	

	8.2.1.2
	Soldered Connections  R8-34 [700] – R8-35 [701]
	Yes
	
	No
	
	
	

	8.2.1.3
	Solderless Wrapped Connections  R8-36 [702]  – R8-43 [709]
	Yes
	
	No
	
	
	

	8.2.2
	Wiring and Cabling R8-44 [710] – R8-48 [714]
	Yes
	
	No
	
	
	

	8.3
	Equipment Modifications
	
	
	
	
	
	

	8.3.1
	General  R8-49 [715] – R8-50 [716]
	Yes
	
	No
	
	
	

	8.3.2
	Modification Wiring  R8-51 [717] – R8-52 [718]
	Yes
	
	No
	
	
	

	8.4
	Performance
	
	
	
	
	
	

	8.4.1
	General  R8-53 [719]
	Yes
	
	No
	
	
	

	8.4.2
	Operation Under Environmental Extremes R8-54 [720]
	Yes
	
	No
	
	
	

	9
	Electrostatic Discharge (ESD)
	
	
	
	
	
	

	9.4
	Circuit Pack ESD Test Methods and Requirements
	Yes
	
	No
	
	
	

	9.4.2.2
	Susceptibility  R9-2 [722]
	Yes
	
	No
	
	
	

	9.4.2.3
	Performance Criteria R9-3 [723]
	Yes
	
	No
	
	
	

	9.4.2.4
	Documentation Specifications R9-4 [724] through R9-7 [727]
	Yes
	
	No
	
	
	

	9.4.3
	Test Preparation R9-8 [728] – R9-9 [729]
	Yes
	
	No
	
	
	

	9.4.5
	Experimental ESD Failure Threshold Measurement
	
	
	
	
	
	

	9.4.5.1
	Required Test Method  R9-10 [730]
	Yes
	
	No
	
	
	

	9.4.5.2
	Equipment Required  R9-11 [731]
	Yes
	
	No
	
	
	

	9.4.5.3
	Waveform Verification Procedure R9-12 [732]
	Yes
	
	No
	
	
	

	9.4.5.5
	Circuit Pack Selection  R9-13 [733]
	Yes
	
	No
	
	
	

	9.4.6
	Documentation of Test Result Definitions and Categories  R9-14 [734] – R9-18 [738]
	Yes
	
	No
	
	
	

	9.5
	ESD Labeling Requirements
	
	
	
	
	
	

	9.5.1.1
	Packaging  R9-19 [739]
	Yes
	
	No
	
	
	

	9.5.1.2
	Equipment  R9-20 [899] – R9-23 [742]
	Yes
	
	No
	
	
	

	9.5.2
	ESD Protective Symbol  CR9-24 [743] – CO9-25 [744]
	Yes
	
	No
	
	
	

	10
	Product Identification & Marking Requirements: R10-1 [747] & O10-26 [772]
	Yes
	
	No
	
	
	

	11
	Package Requirements
	
	
	
	
	
	

	11.1
	General  R11-1 [773] – R11-10 [782]
	Yes
	
	No
	
	
	

	11.2
	Shipping of Assemblies  R11-11[783] – R11-16 [788]
	Yes
	
	No
	
	
	

	12
	Repair and Modification of Customer Return Units
	
	
	
	
	
	

	12.1
	General  R12-1 [789] – R12-8 [796]
	Yes
	
	No
	
	
	

	12.2
	Marking  R12-9 [797]
	Yes
	
	No
	
	
	

	12.3
	Repairs  R12-10 [798] – R12-14 [802]
	Yes
	
	No
	
	
	

	13
	Qualification Test Procedures
	
	
	
	
	
	

	13.1
	Corrosiveness of Soldering Fluxes  R13-1 [803]
	Yes
	
	No
	
	
	

	13.1.1
	Preparation of Fluxes for Testing  R13-2 [804] – R13-4 [806]
	Yes
	
	No
	
	
	

	13.1.2
	Test Patterns for SIR and Electromigration Resistance Testing  R13-5 [807]
	Yes
	
	No
	
	
	

	13.1.3.1
	Surface Insulation Resistance (SIR) Test
	
	
	
	
	
	

	13.1.3.2
	Test Procedure  R13-6 [808] – R13-7 [809]
	Yes
	
	No
	
	
	

	13.1.4.1
	Electromigration Resistance Test
	
	
	
	
	
	

	13.1.4.3
	Data Handling  R13-8 [810] – R13-9 [811]
	Yes
	
	No
	
	
	

	13.1.4.4
	Visual Examination  R13-10 [812]
	Yes
	
	No
	
	
	

	13.2
	Polymeric Coatings and Adhesive Materials
	
	
	
	
	
	

	13.2.1
	General  R13-11 [813] – R13-12 [814]
	Yes
	
	No
	
	
	

	13.2.2
	Visual  R13-13 [815]
	Yes
	
	No
	
	
	

	13.2.3
	Adhesion  R13-14 [816] – R13-16 [818]
	Yes
	
	No
	
	
	

	13.2.4
	Corrosion of Copper  R13-17 [819]
	Yes
	
	No
	
	
	

	13.2.6
	Surface Insulation Resistance (SIR) Test
	
	
	
	
	
	

	13.2.6.2
	Test Procedure  R13-18 [812]
	Yes
	
	No
	
	
	

	13.2.7
	Testing for Resistance to Electromigration
	
	
	
	
	
	

	13.2.7.2
	Test Procedure
	
	
	
	
	
	

	13.2.7.3
	Data Handling  R13-19 [821]
	Yes
	
	No
	
	
	

	13.2.7.4
	Visual Examination  R13-20 [822]
	Yes
	
	No
	
	
	

	13.2.8
	Pre-Production Testing  R13-21 [823] – R13-22 [824]
	Yes
	
	No
	
	
	

	13.3
	Separable Connector and Socketed Component Lubricant Qualification
	
	
	
	
	
	

	13.3.1
	Lubricants for Gold-to-Gold or Similar Noble Metallizations  R13-23 [825] – R13-33 [835]
	Yes
	
	No
	
	
	

	13.3.2
	Lubricants for Tin-to-Tin and Solder-to-Solder Separable Connections  R13-34 [836] – R13-41 [843]
	Yes
	
	No
	
	
	

	13.4
	Qualification of Additive Circuitry for Bare  PWB Modifications  R13-47 [849] – R13-53 [855]
	Yes
	
	No
	
	
	

	14
	Tests and Methods
	
	
	
	
	
	

	14.2
	Metal Finishes
	
	
	
	
	
	

	14.2.2
	Noble Metal Contact Finishes
	
	
	
	
	
	

	14.2.2.4
	Finish Adherence  R14-1 [856]
	Yes
	
	No
	
	
	

	14.3
	PWBs
	
	
	
	
	
	

	14.3.1
	Preparation of Cross-Sections  R14-2 [857] – R14-3 [858]
	Yes
	
	No
	
	
	

	14.3.2
	Thermal Shock Testing of Plated Through Holes (PTHs)  R14-4 [900]
	Yes
	
	No
	
	
	

	14.4
	Insulation Resistance Testing
	
	
	
	
	
	

	14.4.4
	Test Procedure  R14-5 [859]
	Yes
	
	No
	
	
	

	14.5
	Solvent Extract Conductivity Testing
	
	
	
	
	
	

	Comments:
	

	

	

	

	

	

	


H. NEBS TEST RESULTS:   

For each Requirement below mark one box (left side) as Not Tested, Partially Conforms, Does not Conform, or Conforms.  Use “Comments” to provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.

H.1.    Spatial Requirements (Required for CLEC & Carrier Applications)

GR-63, Section 2 & 3:
Specifies requirements for physical size of equipment framework, floor loading, line-up, aisle spacing, operations systems, cabling and cable entrance, front/rear access. 
	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.2.    Thermal Requirements   (Required for CLEC & Carrier Applications)

GR-63, Section 4.1 and various (e.g. GR-418, GR-2834, GR-2836):  Specifies temperature, humidity, and altitude range for a controlled or uncontrolled (“hardened”) environments throughout which the equipment must be able to remain operable, and function normally.  Test procedures and criteria vary depending on whether the equipment is being tested for indoor or outdoor installation.  Check Appendix A and the applicable carrier’s clarification document for specific testing requirements.

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.3.    Fire Resistance Requirements (Required for CLEC & Carrier Applications)

GR63, Section 4:     Limits frequency of fires and extent of damage due to the materials used, overheating, short-circuit damage, rate of flame spread, secondary fires from dripping flaming/molten material and smoke corrosivity.  The tests measure fire resistance by observing self-extinguish ability and flame spread of a burning unit.  The equipment’s fire hazard is characterized by measuring the radiant heat flux and heat release. Fire resistance estimates are less desirable than actual tests.  Check Appendix A and the applicable carrier’s clarification document for specific testing requirements.

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.4.    Handling and Transportation Requirements (Required for Carrier Applications)
GR63, Section 4.3:
Ensures that equipment can be shipped without damage and arrives in serviceable condition.

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.5.    Earthquake and Office Vibration Requirements (CLEC - Earthquake only & Carrier Applications - All)

GR-63, Section 4.4:
 Ensures that seismic or building vibrations from adjacent construction, highways, etc., do not cause operational or performance problems. Nearby heavy machinery, heavy construction, heavy industrial equipment, truck/train traffic, building HVAC systems, or standby generators can result in low frequency vibration.  It is important to know if such low frequency vibration will cause long-term troubles such as connectors becoming loose, or short-term problems like disk drive crashes.

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	Earthquake Zone:
	
	(Specify the Earthquake Zone that was tested.)

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.6.    Airborne Contamination (Required for Carrier Applications)
GR-63, Section 4.5: Describes air quality (particulate) conditions under which equipment is expected to operate properly.  Particulate contamination, specifically soluble salts, can combine with water vapor and result in increased corrosion levels.  Organic vapors and reactive gases can aggravate corrosive actions and can affect disk drive and magnetic tape reliability. Hygroscopic dust contamination creates the potential for resultant intermittent or erratic performance.  Test procedures and criteria vary depending on whether the equipment is being tested for indoor or outdoor installation.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.7.    Acoustic Noise Requirements (Required for CLEC & Carrier Applications)

GR-63, Section 4.6: Limits noise levels than can emanate from equipment.  This requirement is intended to ensure that OSHA limits are not exceeded. 

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.8.    Illumination Requirements (Required for Carrier Applications)

GR-63, Section 4.7:  Establishes requirements for surface reflectance and color intended to minimize reflected glare. It is intended to determine the readability of the stenciling and markings on the equipment, under the ambient light level normally encountered in CO equipment space. Surface finishes and colors, marking colors, styles, size shall be clear and of high contrast and low glare. This requirement does not refer to lighting fixtures supplied or ambient light levels generated by the equipment.

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.9.    ESD and EFT Immunity Requirements (Required for Carrier Applications)

GR-1089, Section 2:  Ensures that equipment operation is not susceptible to ESD and EFT when normally accepted precautions are used.  The requirement is to do the tests.  The objective is to pass the test.  Lab test reports MUST specifically describe equipment functionality during the test discharges.  ANY abnormal or unexpected behavior or system degradation MUST be described.  Emphasis will be placed on the degree of service degradation. 

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.10.    EMI Emission Requirements (Required for CLEC & Carrier Applications)

GR-1089, Section 3.2:  Ensures that equipment does not emit excessive radiated or conducted emissions that could interfere with the proper operation of other equipment. Lab test reports must clearly show the emissions from the equipment, plotted against the acceptable GR‑1089 limits, with the ambient background measurements overlaid on the graph.  Graphs shall be color coded for clarity. 

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


	Are external ferrites required for EMI Emission compliance? (Yes/No)
	


H.11.    EMI Immunity Requirements (Required Carrier Applications)
GR-1089, Section 3.3:
Ensures that the equipment functions properly and that operation is not susceptible to radiated or conducted emissions from other equipment.  Lab test reports MUST specifically describe equipment functionality during the test.  ANY abnormal or unexpected behavior or system degradation MUST be described.  Emphasis will be placed on the degree of service degradation.  
	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


	Are external ferrites required for EMI Immunity compliance? (Yes/No)
	


H.12.    Lightning and AC Power Fault Requirements (Required for CLEC & Carrier Applications)

GR-1089, Section 4:
Prevents or safely limits trouble when equipment is exposed to abnormal or fault conditions resulting from lightning surges and AC power fault conditions that may occur at network terminations.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.13.    Steady-State Power Induction Requirements (Required for Carrier Applications)
GR-1089, Section 5:
Establishes requirements for equipment tolerance of induced, longitudinal (common mode) noise that may be experienced in telephone outside plant facilities.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.14.    DC Potential Difference Requirements (Required for Carrier Applications)
GR-1089, Section 6:
Establishes requirements to ensure that equipment can operate properly when presented with a normally expected potential difference.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.15.    Electrical Safety Requirements (Required for CLEC & Carrier Applications)

GR-1089, Section 7:
Ensures that people using or working on or near the equipment are not exposed to hazards.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.16.    Corrosion Requirements (Required for Carrier Applications)
GR-1089, Section 8:
Ensures that a zero or negative potential with respect to ground is maintained to prevent corrosion in outside plant cables when water accidentally enters the cable core.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.17.    Bonding and Grounding Requirements (Required for CLEC & Carrier Applications)

GR-1089, Section 9:  Ensures that safe and proper operation of this and other equipment is maintained. If this equipment or any component with a physical or electrical connection to this equipment is to be placed within the switch Isolated Ground Plane, conformance to GR-295-CORE (Isolated Ground Plane, Single Point Ground System) is required or Carrier NEBS Compliance approved mitigation measures must be used.  All grounding and bonding conductors must be of sufficient size, as described in GR-295-CORE and must use 2‑hole crimp lugs based on conductor size.  Reference shall be made to GR-1089 R9-9 [79] for acceptable safety Frame Ground connection.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.18.    Criteria for DC Power Port of Telecommunications Load Equipment (Required for CLEC & Carrier Applications)

GR-1089, Section 10:  Establishes requirements to ensure that equipment can operate properly when presented with a normally expected DC Power conditions that may occur on the Ports of the Load Equipment.  

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.19.    GR-487 Requirements for Electronic Equipment Cabinets (Required for Carrier application of outdoor cabinets)

GR-487:
Ensures safe and proper operation of telecom equipment to be placed in an outdoor environment.  The product requires testing to appropriate GR-63 and GR-1089 requirements as directed and augmented by GR-487.
	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	


	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	


H.20.    Energy Efficiency (Required for Carrier Applications) 

VZ.TPR.9205:
Energy Efficiency Requirements for Telecommunications Equipment (Verizon requirement)

ATIS-0600015.2009 Energy Efficiency for Telecommunications Equipment: Methodology for Measurement and Reporting – General Requirements

	Test Facility Name:
	
	Test Date:
	

	Report Number:
	
	Report Date:
	

	Test Results:

	
	Not Tested
	
	Partially Conforms
	
	Does Not Conform
	
	Conforms

	Comments:  
	

	
	

	

	
	

	
	

	
	

	
	

	
	

	
	

	
	


�Telephony power plants are generally referred to as -48vDC systems.  These plants generally operate (a.k.a. float) at -52v to -54v DC with an equalize mode in some reaching -57v DC. All equipment is expected to operate normally in these ranges and shall operate without faults on a reduced supply voltage as low as -42v DC.  Supply voltages between -48v DC and -42v DC may be encountered during abnormal periods when the battery plant may be in a discharging mode as a result of power failures.








VZ.NEBS.TE.NPI.2004.015
June 2018


Page - 1

