Telecommunications Carrier Group

Network Equipment-Building Systems (NEBS)

Compliance Checklist

November 4, 2009

Change Control Record:

| Version | Date | Action* | Reason for Revision |
| --- | --- | --- | --- |
| 1 | 5/1/2004 | New | New document. |
| 2 | 8/11/2004 | Revised | Added Power Drain and Return Current query to Power Requirements |
|  |  |  | Added air filter query to Heat Release Requirements. |
|  |  |  | Reworded sections H.2, H.3, H.6. Added Sections H.19, H.20, H.21. |
| 3 | 12/8/2004 | Revised | Added GR-487 to list of documents in section 3.8.1. |
|  |  |  | Added Earthquake Zone entry to section H.5 |
| 4 | 4/4/2006 | Revised | Changes for SBC AT&T combination. |
| 5 | 9/8/2006 | Change | Modified to take into account the changes in the most recent revision of GR-63-CORE Issue 03; March 2006. |
|  | 9/8/2006 | Change | Modified to take into account the changes in the most recent revision of GR-1089-CORE Issue 04; June 2006. |
|  | 9/14/06 | Revised | Added ANSI T1.336-2003 Requirements |
| 6 | 11/4/09 | Revised | Modified to remove references to Bell South, update to cover GR-1089-CORE Issue 5 and made other minor editorial changes |
| * New, Add, Delete, Change |  |  |  |

Prepared By:

| Name, Title, Organization | Date |
| --- | --- |
| Signature on File Verizon, Todd Talbot, DMTS, NEBS Compliance |  |

Participating Carriers:

| Company, Contact | Date |
| --- | --- |
| Signature on File Verizon, Chuck Graff, Director, NEBS Compliance |  |

| Company, Contact | Date |
| --- | --- |
| Signature on File AT&T Services, Inc., Bon Pipkin, Associate Director, Common Systems Standards |  |

| Company, Contact | Date |
| --- | --- |
| Signature on File Qwest Communications, Fred Camarillo, Manager, Technology Management |  |

TELECOMMUNICATIONS CARRIER

NEBS REQUIREMENTS

1.	TELECOMMUNICATIONS CARRIER GROUP	4

2.	WHY THE TELECOMMUNICATIONS CARRIER NEBS COMPLIANCE CHECKLIST?	4

3.	NEBS INFORMATION	4

3.1.	OVERVIEW	4

3.2.	NEBS REQUIREMENTS	4

3.3.	DEFINITION OF REQUIREMENT AND OBJECTIVE	5

3.4.	CARRIER NEBS REQUIREMENTS COMPARED TO COLLOCATION NEBS REQUIREMENTS	5

3.5.	COPYRIGHT, OWNERSHIP AND PERMISSIONS	5

3.6.	SUBMISSION OF CARRIER CHECKLIST APPENDIX CAND OTHER DATA	5

3.7.	TESTING COMPARED TO DESIGN INTENT	7

3.8.	OBTAINING NEBS GENERIC REQUIREMENTS DOCUMENTS	7

3.9.	EQUIPMENT TESTING	8

3.10.	MAINTAINING NEBS COMPLIANCE	11

3.11.	COMPLIANCE REQUIREMENT	11

4.	WHERE TO REQUEST NEBS COMPLIANCE INFORMATION OR SEND NEBS CHECKLISTS, REPORTS AND DATA	12

APPENDIX A – Requirements Matrix

APPENDIX B - Test Report Certification

APPENDIX C – NEBS Compliance Checklist

# TELECOMMUNICATIONS CARRIER GROUP

## The Telecommunications Carrier Group (TCG) was formed to provide information to manufacturers and help synchronize NEBS testing of telecommunications equipment across the industry.  It is a voluntary consortium open to all telecommunications service providers.  The information presented in this checklist provides a guide to each carrier’s requirements.  Any carrier may change requirements or adopt new requirements without notification to this body.  The participants in the TCG also agree to accept the testing methodologies of the cited requirements.

# WHY THE TELECOMMUNICATIONS CARRIER NEBS COMPLIANCE CHECKLIST?

## All equipment deployed in a carrier’s Central Office (CO) equipment space or data rooms must be safe and pose no risk or safety hazard to any personnel, other nearby equipment or the physical structure.  The carrier also requires that equipment used for service to its customers must be able to deliver dependable and reliable performance during the conditions encountered under normal and abnormal circumstances.

## Equipment compliance to Network Equipment Building Systems (NEBS) generic requirements and other recognized industry standards are the mechanisms used to provide this safety and reliability.  Some NEBS testing and design requirements help make the equipment operate properly and safely; other NEBS requirements enable lower initial and ongoing operating costs for the carrier.

## NEBS is recognized by financial risk assessors, municipalities and regulatory agencies as a major factor in a carrier’s ability to provide reliable, safe and cost efficient service to its customers.  Loss management and municipal agencies recognize the value of NEBS in reducing hazardous conditions and liability risks.  A lack of NEBS compliance could raise the cost of deployment of a given product a prohibitive amount.

## The NEBS requirements allow a carrier to use a single, uniform set of rules to evaluate fairly and impartially all equipment to be placed in the central office environment – whether the equipment is owned by the carrier or placed in leased space by other companies.

## The Telecommunications Carrier NEBS Compliance Checklist is a compendium of what the TCG believes are best industry practices, and do not necessarily reflect all carriers’ criteria or policies.  It is intended to help telecommunications carriers, equipment suppliers and independent testing laboratories by providing a first step toward a complete, common, standardized reference for NEBS compliance testing.

# NEBS INFORMATION

## OVERVIEW

### This document is intended to assist carrier and CLEC suppliers in understanding and meeting NEBS requirements and to explain or clarify carrier concerns and expectations.  Pass/fail criteria for the tests cited may differ between carriers; CHECK WITH SPECIFIC CARRIER FOR THEIR CRITERIA.

### The NEBS requirements are described in GR-63-CORE, GR-1089-CORE, GR-78-CORE, ANSI T1.307, ANSI T1.315 and ANSI T1.319.

### This document may be revised without notice.  The current version of this document is always available on the Verizon NEBS web page http://www.verizonnebs.com and AT&T NEBS web page https://ebiznet.sbc.com/sbcnebs/.

## NEBS REQUIREMENTS

### Carriers DO NOT waive NEBS requirements.  All applicable requirements must be tested.  No test facility, supplier, or consultant may decide what requirements or objectives may be altered or omitted unless the carrier’s NEBS compliance organization is consulted in advance.

### Carriers reserve the right to determine which requirements or objectives may or may not be required.  See Appendix A, Telecommunications Carriers’ NEBS Requirements.  Certain NEBS requirements may not be applicable for all equipment/systems under certain conditions.

#### A detailed explanation the reason the requirement is not applicable shall be provided.

#### The carrier’s NEBS compliance organization will determine the suitability of such explanations.

#### The final determination of all issues regarding applicability, pass/fail requirements or intent shall be decided by the carrier’s NEBS compliance organization.

### All equipment that is being evaluated for NEBS compliance for use by the carrier or a collocator must meet the current NEBS requirements that are in effect at the time the equipment is being evaluated for deployment, not the time the equipment was tested.

## DEFINITION OF REQUIREMENT AND OBJECTIVE

### GR-63, GR-1089 and others list the required tests under the following designations:

#### Mandatory Requirement (R): Testing is required; passing is required.

#### Objective (O) desired requirement: Testing is required; passing is the objective unless otherwise noted in this document.

#### Conditional Requirement (CR): Same as ‘Mandatory Requirement’, however, certain conditions as determined by the carrier may apply.

#### Conditional Objective (CO): Same as ‘Objective’, however, certain conditions as determined by the carrier may apply,

## CARRIER NEBS REQUIREMENTS COMPARED TO COLLOCATION NEBS REQUIREMENTS

### Check with individual carrier for specific requirements for collocated equipment.

## COPYRIGHT, OWNERSHIP AND PERMISSIONS

### The Telecommunications Carrier Group (TCG) holds all copyrights regarding this document.  TCG hereby grants permission to other companies to use this NEBS Requirements document and Appendices for the purpose of providing a standardized method to submit certain data necessary for NEBS compliance analysis.  TCG retains all ownership rights to this document and Appendices as well as all previous versions and reserves the right to make future revisions from time to time.  This paragraph shall be included in all copies or uses.

## SUBMISSION OF CARRIER CHECKLIST APPENDIX B AND OTHER DATA

### The carrier may use the NEBS Compliance Checklist Appendix B to initiate assessment of equipment to be deployed within carrier network equipment space.  TCG participants agree that they will accept documentation presented in this format.  Other formats may be acceptable to individual carriers.

### Product acceptance will be based on compliance of a supplier’s specific product to the requirements specified in the documents listed in Section 3.8.1, Table 2, as indicated in Appendix A.

### Additional carrier requirements, pass/fail criteria and clarifications are identified in the appropriate company specific documents listed in Section 3.8.1 Table 2.

### If used, the NEBS Compliance Checklist Appendix C, with all blanks filled in, and associated data and reports, shall be submitted by the supplier to the carrier's NEBS compliance organization.

#### The submitted form shall include an action plan and time schedule for any non-compliant results.

#### The Checklist Appendix C shall be completed using clear and concise wording and terminology.

#### All blank spaces in the Appendix C shall be properly completed or filled in – no abbreviations shall be used.  Partial, incomplete or missing information on a submitted Appendix B will delay the analysis.

#### Pre-printed statements or measurement units may not be altered.  Additional information shall be submitted via additional pages as needed.

#### “Design Intent, Conforms by Design, Conforms by Analysis” and other similar phrases are generally considered to be ambiguous claims and are inadequate explanations.

#### Ambiguous abbreviations, e.g., N/A, shall be avoided when completing Appendix B.  If “Not Applicable” is used a detailed explanation is required.

#### Appendix C shall be submitted via e-mail to the carrier.

#### Appendix C shall be submitted with current data, as it is known at the time of submission. A supplemental or updated Appendix C may be submitted as additional data becomes available.  It is the responsibility of the supplier and the appropriate carrier contact person to ensure that supplemental Appendix C submissions and test reports are provided in a timely manner to the carrier NEBS compliance organization.  A supplemental or updated Appendix C may be provided as work progresses and shall clearly indicate new or changed information. New or additional data shall be clearly, e.g., bold, italic, highlighted, color, etc., noted on the subsequent submittals.

#### All test data and lab reports submitted to the carrier shall be preceded or accompanied by a current version of the Carrier NEBS Compliance Checklist Appendix B.

#### Any Appendix C received that does not include the specific project or application for the product and a carrier contact person for the product will be considered to be unsolicited material and may not be reviewed.  Please note that members of the carrier NEBS Compliance team are not the carrier contact interested in using the product.

#### The NEBS Compliance Checklist Appendix B, Item A Project Application/Description shall indicate the intended application/location for the equipment installed in the carrier’s facilities.  For example, the Item A shall indicate if the HOST/REMOTE, COT/RT, etc. equipment will be installed in carrier CO space.

#### Only the Appendix B, not this entire document, fully and properly completed shall be submitted. Any blank space is generally considered to be missing data.

### Test Report Certification.  A completed Test Report Certification, Appendix B, must be attached to each test report.  The carrier will not accept test reports without accurate and complete certifications.  Please direct any questions to the carrier’s NEBS compliance contact.  Submit reports and certifications to the carrier’s NEBS compliance organization per Section 4.

### Laboratory test reports and videos shall be provided upon completion of testing.  All reports may be provided as color hard copies or Adobe Portable Document Format (pdf) files on CD-ROM.  NOTE: Carriers may have specific instructions for data presentation.

### The carrier’s NEBS compliance organization will review the Appendix C and all supporting data to determine product acceptability based solely on that carrier’s NEBS compliance organization’s interpretation of the intent of the applicable requirements.

### The carrier’s NEBS compliance organization may work directly with the supplier to resolve any compliance issues identified in the data provided.  However, the carrier contact person will be responsible to ensure that the supplier fulfills the requirement to provide the data.

## TESTING COMPARED TO DESIGN INTENT

### Testing is required to prove compliance with NEBS Requirements.  Compliance statements are inadequate without test results or other substantiating information that is acceptable to the carrier’s NEBS compliance organization.

### Under circumstances, as agreed upon by the carrier’s NEBS compliance organization, some carriers may accept certain field experience data.

### The level of compliance of the equipment will be determined upon receipt of the required test data.

### If tests are in progress or planned, a Checklist must be provided and show expected completion dates.

## OBTAINING NEBS REQUIREMENTS DOCUMENTS

### The equipment supplier is expected to obtain the necessary copies of the documents listed below:

| - Telcordia Documents |  |
| --- | --- |
| - GR-63-CORE Issue 03, March 2006 | - NEBS™ Requirements: Physical Protection-Generic Equipment Requirements - -Describes Physical Requirements |
| - GR-63-CORE Issue 02, April 2002 | - Network Equipment Building System – Generic Equipment Requirements - -Superseded by GR-63-CORE Issue 03 |
| - GR-63-CORE Issue 02, April 2002 Errata | - Corrections to the GR-63-CORE Issue 2 developed after meeting with users of the document. |
| - GR-1089-CORE Issue 5, August 2009 | - Electromagnetic Compatibility and Electrical Safety Generic Criteria for Network Telecommunication Equipment: - -Describes EMC, ESD, and Electrical Safety Requirements |
| - GR-1089-CORE Issue 4, - June, 2006 | - Electromagnetic Compatibility and Electrical Safety Generic Criteria for Network Telecommunication Equipment: - -Superseded by GR-1089-CORE Issue 05 |
| - GR-1089-CORE Issue 3, - October, 2002 | - Electromagnetic Compatibility and Electrical Safety Generic Criteria for Network Telecommunication Equipment: - -Superseded by GR-1089-CORE Issue 04 |
| - GR-1089-CORE Issue 3, January 9, 2003 Errata | - Revisions published on January 9, 2003 in the Known Errata and GR-1089-CORE |
| - GR-78-CORE Issue 1, September 1997 | Generic Physical Design Requirements for Telecommunications Products and Equipment: -Describes General Manufacturing Techniques for Equipment Reliability (e.g., connector types; contact mating surfaces; mixed metal avoidance; tin whisker avoidance; circuit trace sizing and spacing; component materials and composition). (Formerly TR-NWT-000078) |
| - GR-487-CORE Issue 2, March 2000 | Generic Requirements for Electronic Equipment Cabinet: -Generic requirements for electronic equipment and broadband cabinets. |
| - GR-3028-CORE Issue 1, December 2001 | Thermal Management In Telecommunications Central Offices: -Provides thermal management information, guidelines, targets, Objectives, and Requirements for equipment manufacturers and service providers for ensuring network integrity. |
| - SR-3580 Issue1, November 1995 | Network Equipment - Building Systems (NEBS) Criteria Levels: -Telcordia grouping of proposed of the proposed generic requirements into functional groups or levels. |
| - TR-NWT-000295 Issue 2, July, 1995 | Isolated Ground Planes: Definition and Application to Telephone Central Offices. |
| - TR-NWT-000357 Issue 2, October, 1993 | Generic Requirements for Assuring the Reliability of Components Used in Telecommunications Equipment |
| ### Visit the Telcordia store, http://telecom-info.telcordia.com/site-cgi/ido/index.html, or contact Telcordia Customer Relations at 8 Corporate Place, Room 3A-184, Piscataway, NJ 08854-4156, 800-521-2673, 732-699-5800 for further information. |  |
| ### American National Standard (ANSI) Documents |  |
| - T1.307 – 2003 | Fire Resistance Criteria: - Ignitability Requirements for Equipment Assemblies, Ancillary non-metallic Apparatus, and Fire Spread Requirements for Wire and Cable. |
| - T1.315 – 2002 | Voltage Levels for DC-Powered Equipment Used in the Telecommunications Environment |
| - T1.319 – 2002 | Equipment Assemblies – Fire Propagation Risk Assessment Criteria: -Describes test methodology and pass/fail criteria for fire propagation |
| - T1.329-2000 | Network Equipment – Earthquake Resistance |
| - T1.336-2003 | Engineering Requirements for A Universal Telecom Frameworks |
| ### Visit the ANSI eSTANDARDS STORE at http://webstore.ansi.org/ansidocstore/default.asp for further information. |  |

Table 1

### The documents listed below provide carrier specific clarifications to NEBS testing and evaluation process.  The equipment supplier is expected to obtain copies of the documents listed below as necessary:

| ### Verizon Clarification Documents: |  |  |
| --- | --- | --- |
| - VZ.TPR.9305 |  |  |
| ### Visit the Verizon NEBS Compliance Web Page at http://www.verizonnebs.com/. |  |  |
| ### AT&T Clarification Documents: |  |  |
| - TP 76200 |  |  |
| - ESP forms |  |  |
| Visit the AT&T NEBS Compliance Web Page at https://ebiznet.sbc.com/sbcnebs/. |  |  |
| ### Qwest Clarification Documents: |  |  |
| - Pending |  |  |
| ### Visit the Qwest Technical Publications Web Page at http://www.qwest.com/techpub/. |  |  |

Table 2.

## EQUIPMENT TESTING

### TEST FACILITY AND CHARGES

#### The supplier shall be responsible for all costs/charges associated with compliance testing.

#### The telecommunication carriers participating in this document will accept the test procedures referenced here.  Other carriers may have different requirements for lab testing.  Please contact the appropriate carrier for detailed information before beginning equipment testing to make certain your test plans meet requirements.  Test results that do not meet carrier requirements will not be accepted.

### TEST DOCUMENTATION

#### The NEBS Compliance Checklist Appendix C is a vehicle for reporting product and testing information, but is not accepted without supporting test data.

#### The supplier must furnish sufficient documentation to substantiate to the carrier’s NEBS compliance organization that NEBS testing was done per the stipulated procedures, methods, and ranges in the NEBS family of documents, referenced in Section 3.8.1.

#### Suppliers shall ensure that the selected test facility is familiar with the documentation criteria noted throughout this document and is acceptable to the carrier’s NEBS compliance organization

#### The carrier NEBS compliance organization will not return test reports and videos.

#### Lab reports, written documentation, fire spread and earthquake videos, etc. shall specifically reference the appropriate GR-63, GR-1089, GR-78 section(s) covered by the report.

#### Lab reports shall specifically report test results by referencing the appropriate GR Requirement (R) or Objective (O) numbers.  Paragraph numbers are optional.  See Section 3.2.

#### Lab reports and documentation shall report test conditions and observed characteristics of the equipment during testing.  Explanations of conditions and reactions shall be included as appropriate, including descriptions of failures and errors and the impact on the functional performance of the equipment.  Reports shall refrain from injecting opinions into the body of the observations.  Opinions may be grouped together in a specifically labeled report section.

#### Tested equipment configurations and a list of all equipment modules used in the test configurations shall be included.  The list shall include the module name/designation, model number, and part/ordering number. Any equipment modules not used in a tested configuration shall be listed as not tested.

#### Test data, reports, and videos shall be submitted complete and intact, that is, as originally printed and bound by the test facility.  Reports that are missing information or are re-packaged by a supplier may not be acceptable.

#### Suppliers and lab facilities are reminded that a Root Cause Analysis (RCA) is required for all tests that have failed, including those of GR-63-CORE, GR-1089-CORE and the tests specified in this document, even if subsequent re-testing is successful. (GR-63; R4-1, R4-2)

##### RCAs must include an explanation of what failed, why it failed (i.e., what caused the cause of the failure) and corrective action description.

##### Manufacturing cut-in dates, serial numbers, product ID changes, ordering requirements, availability, etc. for equipment incorporating the corrective action shall be included in RCAs.

### TEST METHODS or PROTOCOLS

#### The NEBS Generic Requirements documents describe the procedures, methods and range criteria to be used to do the NEBS tests and the acceptable test result limits.  Suppliers and test labs are cautioned not to omit or modify portions of the test(s) without the carrier’s NEBS compliance organization’s prior agreement.

#### Compliance requires that the tests be performed as described in GR-63 and GR-1089 or other specifications and that the results meet the described limits.

#### Many of the various elements have multiple subsections and criteria.  If any of these subsections do not fully conform to the requirements, the entire section does not conform.  The supplier shall report data by subsection if necessary.

#### Suppliers and test labs are cautioned not to abort a test in progress simply because a segment or requirement failed to pass.  The errors, failure mode, symptoms and performance shall be documented in the report.  The failure mode and data are important in analyzing the ability of the equipment to function under the potential marginal conditions represented by the test.

#### Suppliers’ or manufacturers’ internal corporate standards and requirements are generally considered to be insufficient as a gating pass/fail requirement.  Use of these standards requires prior agreement with the carrier’s NEBS compliance organization and the standards must fully and specifically reference the NEBS family of documents.

### SUPPLIER ACTION PLANS

#### For elements that “CONFORM,” provide a copy of the laboratory test data.

#### For elements that “FAIL to CONFORM,” provide a copy of the laboratory test data, an action plan and an explanation indicating when and how Compliance will be attained.

#### For elements that “PARTIALLY CONFORM,” provide a copy of the laboratory test data, an action plan and an explanation indicating when and how compliance will be attained.

#### Suppliers or manufactures shall provide detailed explanations of the reason any elements were not tested.  In general, all elements must be tested; however, there may be specific circumstances where testing may not be required.

### EQUIPMENT CONFIGURATION

#### Suppliers shall ensure that the equipment to be tested is arranged so that all equipment slots or positions, e.g., circuit pack slots, are fully equipped to a worst case configuration with regard to floor load, heat release, fire resistance, fuel load, etc. The configuration shall include all representative circuit packs likely to be used or encountered by the carrier, even if the slot normally contains a circuit pack that is not being evaluated as part of the current test sequence.   Once the configuration intended for the carrier is reached, the supplier may add additional PCBs that could be used in the equipment for different applications.

#### Refer to GR-1089, Section 3.5.5, Item 3 “The EUT power and signal leads shall be, as nearly as possible, of the same length, orientation, and termination as they are in their normal operational configuration.”

#### Equipment shall be functioning, except for the fire spread tests, using acceptable call processing, application or load generating software that simulates normal traffic or operational loads.  Diagnostic exercises are generally not sufficient.

#### Equipment may not be functionally tested at a unit or shelf level unless it can properly perform the intended deployed function and is representative of the installed configurations likely to be encountered. Specifically, multi-shelf systems (e.g., a control unit and the units controlled) shall be tested at the frame level.

#### All workstations, terminals, monitors, modems, alarm units, ringing and tone generators, etc. that may be required for the equipment being tested and are permanently installed, i.e., ‘left in place,’ shall be included in the equipment test configurations.

#### Suppliers are encouraged to verify test plans and configurations with the carrier’s NEBS compliance organization before tests are done, to ensure the test configurations will be acceptable to the carrier.  Test plans shall list all tests, provide detailed card layouts and indicate test points.  If a test is not being performed, it shall still be listed and an explanation provided of why the test is not being performed.

#### If a supplier has a shelf level product but anticipates that multiple units will be used in a specific application, then the appropriate number of units shall be placed in a rack and tested together as a system.  The carrier may not accept individually tested shelf units when they are combined with other like or different shelves for a specific application.

#### All supplier provided racks, frames and cabinets must be of welded, steel construction and meet the specifications of GR-63 section 3.1 (R3-1) or ANSI T1.336-2003.

### OEM EQUIPMENT

#### The equipment supplier is responsible for ensuring that all OEM (Original Equipment Manufacturer) devices and subassemblies also meet the NEBS requirements.

#### The use of an OEM component or subsystem as a part of the larger system/application does not relieve any NEBS criteria.

#### The supplier or integrator of the final system or application provided to the carrier is responsible for attaining and maintaining NEBS Compliance.

#### The supplier or integrator of the final system or application provided to the carrier may provide the OEM’s test data if authorized by the OEM.  However, if the OEM equipment is integrated in a rack configuration with other equipment, the entire configuration must be NEBS tested.

## MAINTAINING NEBS COMPLIANCE

### The supplier is responsible for ensuring that NEBS Compliance is maintained throughout the equipment’s deployed service life in the carrier.  Specifically, it is the supplier’s responsibility to ensure that replacement repaired or redesigned parts continues to meet the NEBS requirements.  The NEBS checklist Appendix C shall be resubmitted after every NEBS effecting change as determined by an ITL.  Examples of possible NEBS effecting changes include microprocessor changes, printed circuit board changes, component modifications and substitutions, back-plane modifications, enclosure modifications, etc.

## COMPLIANCE REQUIREMENT

### Lack of substantiating data, as described in this document, will be considered non-compliance.  All equipment considered for deployment in carrier Central Office equipment space will be evaluated based on compliance to all NEBS requirements.  See Section 3.2.

### NEBS compliance must be demonstrated by testing to the requirements in GR-63-CORE, GR-1089-CORE and carrier requirements as noted in Appendix B.  These documents describe the test methods and procedures and the expected test result limits.

### No supplier or test facility shall base compliance on the use of a cabinet or enclosure to contain EMI or fire spread.  That is, cabinets shall not be relied upon to act as a barrier.  The equipment must meet the requirements.  Under certain conditions, the carrier’s NEBS compliance organization may prescribe the use of such cabinetry only as a (limited) mitigation measure.

### The supplier is expected to maintain NEBS Compliance for the product, throughout the equipment service life in the carrier, as described in TR-NWT-000357.

# WHERE TO REQUEST NEBS COMPLIANCE INFORMATION OR SEND NEBS CHECKLISTS, REPORTS AND DATA

- All requests for NEBS compliance information or checklists shall be sent to the appropriate company contact listed below or as provided by the carrier.

- E-mailing a checklist will expedite analysis.

Verizon

Chuck Graff - Verizon Laboratories,

Director NEBS Compliance & Quality Assurance

320 St. Paul Place, 4th Floor

Baltimore, MD 21202

Tel:  410-736-5904

Fax: 410-736-5144

E-mail: Ludwig.C.Graff@Verizon.com

AT&T

John Tablerion

NEBS Evaluation Coordinator

15248 South Rivina, Rm 1

Orland Park, IL 60462

Tel: 708-403-4450

E-mail: jt3216@att.com

Qwest

Fred Camarillo

Manager Technology Management

700 W. Mineral

Littelton CO. 80120

E-Mail:  Fred.Camarillo@Qwest.com

Tel: 303-707-7076

APPENDIX A.       													 Requirements Matrix

A:  General Information

The following matrices list the various GR-63-CORE and GR-1089-CORE requirements and objectives followed by columns listing each company’s specific comments.  The company specific comments can be interpreted according to the following key.

| EC | Evaluation Clarification Required (See Section 3.8.2.) |
| --- | --- |
| ENR | Evaluation Not Required |
| ER | Evaluation Required |
| TBD | To Be Determined |

Table 1

B:  GR-63-CORE Requirements, Issue 3 March 2006

| Section | Section Name | Criteria | Verizon | AT&T | Qwest |
| --- | --- | --- | --- | --- | --- |
| 2 | Spatial Requirements | - | - | - | - |
| 2.1 | General Requirements | - | - | - | - |
|  | Hole Pattern | R2-1 [1] | ER | ER | ER |
|  | Anchoring Method | R2-2 [2] | ER | ER | ER |
|  | Equipment Entrance | R2-3 [3] | ER | ER | ER |
|  | One Depth | O2-4 [4] | ER | ER | ER |
|  | Horizontal extension | R2-5 [5] | ER | ER | ER |
|  | Leveling capabilities | R2-6 [6] | ER | ER | ER |
|  | Alignment | O2-7 [7] | ER | ER | ER |
|  | Clearance | O2-8 [8] | ER | ER | ER |
| 2.1.1 | Equipment Frame Floor Plans | - | - | - | - |
|  | Floor Plans | O2-9 [9] | ER | ER | ER |
|  | Maximum Asile Spacing | R2-10 [146] | ER | TBD | TBD |
|  | Minimum Asile Spacing | R2-11 [147] | ER | TBD | TBD |
|  | Equipment Functionality | O2-12 [10] | ER | ER | ER |
|  | Raised Floors | O2-13 [11] | ER | ER | ER |
| 2.1.2 | NEBS Data (ND) | - | - | - | - |
|  | Deleted | R2-14 [12] | - | - | - |
| 2.2 | Equipment Frames | - | - | - | - |
| 2.2.2 | Equipment Frame Dimensions | - | - | - | - |
|  | Maximum Height | O2-15 [13] | ER | ER | ER |
|  | Open Rack HxWxD | O2-16 [14] | ER | TBD | TBD |
|  | Depth Specification | O2-17 [148] | ER | TBD | TBD |
|  | Fastening Arrangement | O2-18 [149] | ER | ER | ER |
| 2.2.2.2 | Equipment Frame Dimensions (Other) | - | - | - | - |
|  | HxWxD, New Equip or Deeper Chassis | O2-19 [150] | ER | TBD | TBD |
| 2.2.2.4 | Equipment Frame Cable Management Provisions |  |  |  |  |
|  | Cabling Access | R2-20 [151] | ER | TBD | TBD |
|  | Larger Cable Management | O2-21 [151] | ER | TBD | TBD |
| 2.2.2.5 | Equipment Frame Interface with Cable Rack | - | - | - | - |
|  | Fastening Arrangement | R2-22 [15] | ER | ER | ER |
|  | Framework | O2-23 [16] | ER | ER | ER |
| 2.2.3 | Equipment Frame Lineup Conformity | - | - | - | - |
|  | Equipment Frame Lineup Conformity | R2-24 [17] | ER | ER | ER |
| 2.2.4 | Equipment Frame Floor Loading | - | - | - | - |
|  | Equipment Frame Floor Loading | O2-25 [18] | ER | ER | ER |
|  | Overhead CDS | R2-26 [19] | ER | ER | ER |
| 2.2.5 | AC Convenience Outlets Within Equipment Frames | - | - | - | - |
|  | AC Convenience Outlets | R2-27 [20] | ER | ER | ER |
|  | National Electric Code (NEC) | R2-28 [21] | ER | ER | ER |
| 2.3 | Distributing and Interconnecting Frames | - | - | - | - |
| 2.3.1 | Distributing Frames (DFs) | - | - | - | - |
|  | Frame Dimension | O2-29 [22] | ER | ER | ER |
|  | Frame Floor Load | R2-30 [23] | ER | ER | ER |
|  | Overhead Cable | O2-31 [24] | ER | ER | ER |
| 2.4 | DC Power Plant Equipment | - | - | - | - |
| 2.4.1 | Centralized DC Power Plant Equipment | - | - | - | - |
|  | DC Power Heigh | R2-32 [25] | ER | ER | ER |
|  | Superseded by R2-10 [146] | R2-33 [26] | ER | ER | ER |
|  | Frame Floor Load | O2-34 [27] | ER | ER | ER |
|  | Power CDS Structure | O2-35 [28] | ER | ER | ER |
| 2.5 | Cable Distribution Systems (CDSs) | - | - | - | - |
| 2.5.1.2 | Overhead Cable Distribution | - | - | - | - |
|  | Cross Aisle path | O2-36 [29] | ER | ER | ER |
|  | Centering | O2-37 [30] | ER | ER | ER |
|  | Support of Assoc Equipment | O2-38 [31] | ER | ER | ER |
|  | Illumination Requirements | O2-39 [32] |  | ER |  |
|  | System CDS Clearance | O2-40 [33] | ER | ER | ER |
| 2.5.1.3 | Cable Distribution Under Raised Floor | - | - | - | - |
|  | Under floor Cabling NEC | R2-41 [34] | ER | ER | ER |
|  | Under floor CDS | R2-42 [35] | ER | ER | ER |
|  | Cable Segregation | O2-43 [36] | ER | ER | ER |
| 2.5.4 | CDS Floor Load and Support | - | - | - | - |
|  | CDS Floor Load and Support | O2-44 [37] | ER | ER | ER |
| 2.6 | Operations Systems (OSs) | - | - | - | - |
|  | Operations Systems (OSs) | R2-45 [38] | ER | ER | ER |
| 2.7 | Cable Entrance Facility (CEF) | - | - | - | - |
| 2.7.1 | CEF Spatial Requirements | - | - | - | - |
|  | CEF Spatial Requirements | O2-46 [39] | ENR | ER | ER |
| 2.7.2 | CEF Loading Requirements | - | - | - | - |
|  | Floor Loading Requirements | O2-47 [40] | ENR | ER | ENR |
|  | Wall-Supported Weight Limit | R2-48 [41] | ENR | ER | ENR |
| 2.7.3 | CEF Equipment Temperature and Humidity Requirements | - | - | - | - |
|  | CEF Equipment Temperature and Humidity Requirements | R2-49 [42] | ENR | ER | ENR |
| 3 | NEBS-2000 Framework Criteria | - | - | - | - |
|  | See Table F: ANSI T1.336-2003 | The information in this section has been deleted in GR-63-CORE, Issue 3. Please refer to ANSI T1.336-2003, Engineering Requirements for a Universal Telecom Framework for dimensional, performance, and application criteria that may be applied to framework used to support electronic equipment shelves in a telecommunications facility. |  |  |  |
| 4.0 | Environmental Criteria | - | - |  | - |
|  | RCA | R4-1 [67] | ER | ENR | ER |
|  | RCA solution | R4-2 [68] | ER | ENR | ER |
| 4.1 | Temperature, Humidity, and Altitude Criteria | - | - | - | - |
| 4.1.1 | Transportation and Storage Environmental Criteria | - | - | - | - |
| 4.1.1.1 | Low-Temperature Exposure and Thermal Shock | R4-3 [69] | ER | ER | ER |
| 4.1.1.2 | High Relative Humidity Exposure | R4-4 [71] | ER | ER | ER |
| 4.1.1.3 | High-Temperature Exposure and Thermal Shock | R4-5 [70] | ER | ER | ER |
| 4.1.2 | Operating Temperature and Humidity Criteria | - | - | - | - |
|  | Ambient Temperature and Humidity Limits | R4-6 [72] | ER | ER | ER |
|  | Deleted | R4-7 [73] | ER | ER | ER |
| 4.1.3 | Altitude | - | - | - | - |
|  | Altitude to 6000 | R4-8 [74] | ER | ER | ER |
|  | Altitude to 13,000 | R4-9 [136] | ER | ER | ER |
|  | Criteria above 6000 | R4-10 [75] | ER | ER | ER |
|  | Functional to 6000 | O4-11 [137] | ER | ER | ER |
|  | Functional to 13,000 | O4-12 [76] | ER | ER | ER |
| 4.1.4 | Temperature Margin Evaluation |  |  |  |  |
|  | Temperature Response | R4-13 [153] | ER | TBD | TBD |
| 4.1.5 | Fan Cooled Equipment Criteria |  |  |  |  |
|  | Single Fan Failure | R4-14 [154] | ER | TBD | TBD |
|  | Remote Alarm | R4-15 [155] | ER | TBD | TBD |
|  | Cooling Unit Replacement | O4-16 [156] | ER | TBD | TBD |
|  | Replacement Proc. In Documentation | R4-17 [157] | ER | TBD | TBD |
|  | Service Interruption | R4-18 [158] | ER | TBD | TBD |
| 4.1.4 | Heat Dissipation | - | - | - | - |
|  | Maximum Heat Release and Cooling Method | R4-19 [77] | ER | ER | ER |
|  | Heat Release | O4-20 [78] | ER | EC | EC |
| 4.1.7 | Surface Temperature | - | - | - | - |
|  | Aisle Facing Surfaces (> 48C) | O4-21 [79] | ER | ER | ER |
|  | Aisle Facing Surfaces (per Table) | R4-22 [159] | ER | TBD | TBD |
| 4.1.8 | Equipment Airflow | - | - | - | - |
|  | Airflow Schemes (approved) | O4-23 [160] | ER | ER | TBD |
|  | Airflow Schemes (not approved) | 04-24 [161] | ER | ER | TBD |
| 4.2 | Fire Resistance | - | - | - | - |
| 4.2.2 | Equipment Assembly Fire Tests | - | - | - | - |
| 4.2.2.1 | Frame-Level Fire-Resistance Criteria | - | - | - | - |
|  | A. Fire spread Criteria | - | - | - | - |
|  | Deleted | R4-25 [80] | EC | ENR | EC |
|  | Flame Spread | R4-26 [81] | EC | ER | EC |
|  | Excessive Surface Burning | R4-27 [162] | ER | ER | TBD |
|  | B. Fire Propagation Hazard Characterization | - | - | - | - |
|  | Rate Of Heat Release | R4-28 [82] | ER | ENR | TBD |
|  | Peak Heat Release | O4-29 [83] | EC | ENR | EC |
|  | Average Heat Release | O4-30 [84] | EC | ENR | EC |
| 4.2.2.2 | Shelf-Level Fire-Resistance Criteria | - | - | - | - |
|  | A. Fire spread Criteria | - | - | - | - |
|  | Deleted | R4-31 [85] | EC | EC | EC |
|  | Flame Spread | R4-32 [86] | EC | ER | EC |
|  | Excessive Surface Burning | R4-33 [163] | ER | ER | TBD |
|  | B. Fire Propagation Hazard Characterization | - | - | - | - |
|  | Rate Of Heat Release | R4-34 [87] | EC | ENR | EC |
|  | Peak Heat Release | O4-35 [88] | EC | ENR | EC |
|  | Average Heat Release | O4-36 [89] | EC | ENR | EC |
| 4.2.2.3 | Smoke and Self-Extinguishment Criteria | - | - | - | - |
|  | 4min 30sec., Start to Self Extinguish | O4-37 [164] | ER | ENR | TBD |
|  | 10min, Flame Reduction | O4-38 [165] | ER | ENR | TBD |
|  | 15min, Flames Extinguished | R4-39 [166] | ER | ER | TBD |
|  | 15min, Minimal Wisps of Smoke | O4-40 [167] | ER | ENR | TBD |
|  | 20min, No Visibal Smoke | R4-41 [168] | ER | ER | TBD |
| 4.2.3 | Use of Fire-Resistant Materials, Components, Wiring, and Cable | - | - | - | - |
| 4.2.3.1 | Material/Comp. Fire-Resistance Criteria | - | - | - | - |
|  | Fire Resistance | R4-42 [90] | ER | ER | ER |
|  | A. Mechanical Elements | - | - | - | - |
|  | UL 94 / ASTM D 2863-77 | R4-43 [91] | ER | ER | ER |
|  | Needle Flame | R4-44 [92] | ER | ER | ER |
|  | UL 94 | R4-45 [93] | ER | ER | ER |
|  | Deleted | R4-46 [94] | - | - | - |
|  | UL –510 | R4-47 [95] | ER | ER | ER |
|  | UL –1441 | R4-48 [96] | ER | ER | ER |
|  | B. Electronic Components |  |  |  |  |
|  | Electrical Components | R4-49 [97] | ER | ER | ER |
|  | C. Interconnect Wire | - | - | - | - |
|  | UL –1581 | R4-50 [98] | ER | ER | ER |
|  | Deleted | O4-51 [99] | - | - | TBD |
| 4.2.3.2 | Cable Distribution Assemblies | - | - | - | - |
|  | Deleted | R4-52 [100] | ER | ER | TBD |
|  | - Plenum Space Wire and Cable | R4-53 [101] | ER | ER | ER |
|  | B. Riser Shaft Wire and Cable | R4-54 [102] | ER | ER | ER |
|  | C. Communication and Power Wire and Cable | R4-55 [103] | ER | ER | ER |
|  | D. Limited Smoke Wire and Cable | O4-56 [104] | ER | ENR | ER |
|  | E. AC-Powered Wiring and Fittings | R4-57 [105] | ER | ER | ER |
| 4.2.4 | Smoke Corrosivity (Deleted) | O4-42 [106] | - | - | - |
| 4.2.4.1 | Optical Fiber Cable Trays and Raceways |  | - | - | - |
|  | - Optical Fiber Cable Tray/Raceway in Duct or Plenum Spaces | R4-59 [169] | ER | ER | TBD |
|  | - Optical Fiber Cable Tray/Raceway in Riser shafts | R4-60 [170] | ER | ER | TBD |
|  | - Optical Fiber Cable Tray/Raceways in Other Spaces | R4-61 [171] | ER | ER | TBD |
|  | - Ignitability Requirements for Ancillary Materials | - | - | - | - |
|  | Surface Area < 1 ft2 | R4-62 [172] | ER | ER | TBD |
|  | Surface Area > 1 ft2 | R4-63 [173] | ER | ER | TBD |
|  | Surface Area < 10 ft2 | R4-64 [174] | ER | ER | TBD |
| 4.3 | Equipment Handling Criteria | - | - | - | - |
| 4.3.1 | Packaged Equipment Shock Criteria | - | - | - | - |
| 4.3.1.1 | Category A Containers | R4-65 [107] | ER | ER | ER |
| 4.3.1.2 | Category B Containers | R4-66 [108] | ER | ER | ER |
| 4.3.2 | Unpackaged Equipment Shock Criteria | R4-67 [109] | ER | ER | ER |
| 4.4 | Earthquake, Office Vibration, and Transportation Vibration | - | - | - | - |
| 4.4.1 | Earthquake Environment and Criteria | - | - | - | - |
|  | Waveform Testing per 5.1 | R4-68 [110] | ER | ER | ER |
|  | Amplitude Deflection | R4-69 [111] | ER | ER | ER |
|  | Natural Mechanical Frequency >2.0 Hz | R4-70 [112] | ER | ER | ER |
|  | Natural Mechanical Frequency > 6.0 Hz | O4-71 [113] | ER | ER | ER |
|  | Axis Waveform Testing | R4-72 [114] | ER | ER | ER |
|  | Functional Operation | O4-73 [115] | ER | ER | ER |
| 4.4.2 | Framework and Anchor Criteria | - | - | - | - |
|  | Welded Construction | O4-74 [116] | ER | ER | ER |
|  | Base Mounting | R4-75 [117] | ER | ER | ER |
|  | Static Pull | O4-76 [118] | ER | ER | ER |
|  | Concrete Anchors (max depth) | R4-77 [119] | ER | ER | ER |
|  | Concrete Anchors (dynamic applications) | O4-78 [120] | ER | ER | ER |
|  | Steel Anchors | O4-79 [121] | ER | ER | ER |
| 4.4.3 | Wall-Mounted Equipment Anchor Criterion | - | - | - | - |
|  | Fastners Load criteria | R4-80 [175] | ER | ER | TBD |
| 4.4.4 | Office Vibration Environment and Criteria |  |  |  |  |
|  | Physical Performance Criteria | R4-81 [122] | ER | ER | ER |
|  | Functional Performance Criteria | R4-82 [123] | ER | ER | ER |
| 4.4.5 | Transportation Vibration Criteria | R4-83 [124] | ER | ER | ER |
| 4.5 | Airborne Contaminants | - | - | - | - |
| 4.5.2 | Contamination Levels | - | - | - | - |
| 4.5.2.1 | Environmentally Controlled Space | R4-84 [125] | ER | ER | ER |
|  |  | O4-85 [126] | ER | ER | ER |
| 4.5.2.2 | Outside Plant Equipment | R4-86 [127] | ER | ER | ER |
| 4.5.4 | Equipment-Fan Filters | - | - | - | - |
|  | Fan Filters | R4-87 [138] | ER | ER | ER |
|  | Fan Filters Dust Spec | R4-88 [139] | ER | ER | ER |
|  | Dust Arrestance of 65% or MERV of 2 | R4-89 [176] | ER | ER | TBD |
|  | Fan Filter Fire Rating | R4-90 [140] | ER | ER | ER |
|  | Air Bypass | R4-91 [141] | ER | ER | ER |
|  | Handling Contamination | R4-92 [142] | ER | ER | ER |
|  | Replacement Schedule | R4-93 [143] | ER | ER | ER |
|  | Filter Alarm | O4-94 [144] | ER | ER | ER |
|  | Filter Disposable | O4-95 [145] | ER | ER | ER |
| 4.6 | Acoustic Noise | - | - | - | - |
|  | Acoustical noise Limits | R4-96 [128] | ER | ER | ER |
|  | Fan Sound Power Level | R4-97 [177] | ER | ER | TBD |
| 4.7 | Illumination | - | - | - | - |
| 4.7.1 | Quantity of Light | - | - | - | - |
|  | Minimum Levels of Illuminations | R4-98 [129] | ENR | ENR | ENR |
|  | Illumination Level | O4-99 [130] | ENR | ENR | ENR |
|  | Energy Efficient Lighting System | R4-100 [131] | ENR | ENR | ENR |
| 4.7.1.2 | Luminance Ratios | - | - | - | - |
|  | Luminance Ratios | O4-101 [134] | ER | ER | ER |
|  | Color of Light | O4-102 [135] | ENR | ENR | ENR |
| 4.7.2 | Illumination Criteria for Network Equipment | - | - | - | - |
|  | Surface Reflectance and Color | O4-103 [132] | ER | ER | ER |
|  | Glare | O4-104 [133] | ER | ER | ER |

C:  GR-1089-CORE Requirements, Issue 5 August 2009

| Section | Section Name | Criteria | Verizon | AT&T | Qwest |
| --- | --- | --- | --- | --- | --- |
| 2 | System-Level Electrostatic Discharge | - | - | - | - |
| 2.1.2 | ESD Immunity Criteria | - | - | - | - |
|  | IEC 61000-4-2, Edition 1.2, 2001-04 | R2-1 [1] | ER | ER | ER |
|  | Test to Normal and Inst/Repair | R2-2 [2] | ER | ER | ER |
| 2.1.2.1 | Immunity Criteria – Normal Operation | R2-3 [3] | ER | ER | ER |
| 2.1.2.2 | Immunity Criteria – Installation and Repair | O2-4 [4] | ER | ER | ER |
| 2.1.2.3 | ESD Warning Label Requirements | R2-5 [5] | ER | ER | ER |
| 2.1.2.4 | Equipment Specific Requirements | - | - | - | - |
|  | Additional Equipment Requirements | R2-6 [6] | ER | ER | ER |
|  | Maintenance Information | R2-7 [7] | ER | ER | ER |
| 2.2 | Electrical Fast Transient | R2-8 [126] | ER | ER | ER |
| 3 | Electromagnetic Interference | - | - | - | - |
| 3.1.5 | Documentation | R3-1 [159] | ER | ER | TBD |
| 3.2.1.1 | Electric Fields Radiated Emission Criteria | - | - | - | - |
|  | Closed Door Requirement | R3-2 [8] | ER | ER | ER |
|  | Open Door Objective | O3-3 [9] | ER | ER | ER |
|  | Open Door Requirement | R3-4 [10] | ER | ER | ER |
| 3.2.1.2 | Electric Fields Radiated Emission Criteria for Intentional Radiators | - | - | - | - |
|  | Certified to parts of 47 CFR | R3-5 [160] | ER | ER | TBD |
|  | Closed Door Requirement | R3-6 [161] | ER | ER | TBD |
|  | Fund. Freq. Measurement in Report | R3-7 [162] | ER | ER | TBD |
|  | Open Door Objective | O3-8 [163] | ER | ER | TBD |
| 3.2.1.3 | Magnetic Fields Radiated Emission Requirement | R3-9 [11] | ER | ER | ER |
| 3.2.2.1 | Conducted Emission Requirements for AC Power Ports – Voltage | R3-10 [12] | ER | ER | ER |
| 3.2.2.2 | Conducted Emission Requirements for AC and DC Power Ports – Current | R3-11 [13] | ER | ER | ER |
| 3.2.3 | Conducted Emission Criteria for Telecommunications Ports | - | - | - | - |
| 3.2.3.1 | Conducted Emissions Requirements for Signal Leads – Current | R3-12 [128] | ER | ER | ER |
| 3.2.3.2 | Conducted Emission Requirements For Analog Voiceband Leads | R3-13 [14] | ER | ER | ER |
| 3.2.3.3 | Conducted Emissions Objectives for Telecommunications Leads | R3-14 [129] | ER | ER | ER |
| 3.3.1 | Radiated Immunity Criteria | - | - | - | - |
| 3.3.1.1 | Electric Fields Radiated Immunity Criteria with Doors and Covers Closed | - | - | - | - |
|  | Deleted | R3-15 [15] | - | - | - |
|  | Doors and Covers Closed | R3-16 [16] | ER | ER | ER |
| 3.3.1.2 | Electric Fields Radiated Immunity Criteria with Doors and Covers Open | - | - | - | - |
|  | Deleted | R3-17 [17] | - | - | - |
|  | Perform Properly | R3-18 [18] | ER | ER | ER |
| 3.3.2 | Conducted Immunity Criteria for AC and DC Power Ports | - | - | - | - |
|  | Deleted | R3-19 [19] | - | - | - |
|  | Perform Properly | R3-20 [130] | ER | ER | ER |
| 3.3.3.1 | Conducted Immunity Requirement for Signal Leads | R3-21 [131] | ER | ER | ER |
| 3.3.3.2 | Conducted Immunity Objectives for Voiceband and Telecommunications Leads | R3-22 [164] | ER | ER | TBD |
| 4 | Lightning and AC Power Fault | - | - | - | - |
| 4.5 | Characterization of Test Generators | R4-1 [26] | ER | ER | ER |
| 4.6.2 | Deleted | R4-2 [20] | - | - | - |
| 4.6.2.4 | Test Setup for Equipment Providing or Receiving Remote Power | - | - | - | - |
|  | Lightning surge Test | O4-3 [165] | ER | ER | TBD |
|  | AC Power Fault Test | O4-4 [166] | ER | ER | TBD |
| 4.6.5 | Short-Circuit Tests (Telecommunications Port) | R4-5 [25] | ER | ER | ER |
| 4.6.6 | First-Level Lightning Surge Tests (Telecommunications Type 1,3,and 5 Ports) | - | - | - | - |
|  | No Damage | R4-6 [27] | ER | ER | ER |
|  | Secondary Protector | R4-7 [167] | ER | ER | TBD |
| 4.6.7 | First-Level Lightning Protection Tests (Telecommunications Type 1,3,and 5 Ports) | - | - | - | - |
|  | Deleted | O4-8 [133] | - | - | - |
|  | No Damage | R4-9 [134] | ENR | ER | ER |
| 4.6.8 | Second-Level Lightning Surge Tests (Telecommunications Type 1,3, and 5 Port) | R4-10 [29] | ER | ER | ER |
| 4.6.8.1 | Equipment Ports With Secondary Protection | R4-11 [168] | ER | ER | TBD |
| 4.6.9 | First-Level Intra-Building Lightning Surge Tests (Telecommunications Type 2 and 4 Ports) | - | - | - | - |
| 4.6.9.1 | Ports Connected to Unshielded Cables | - | - | - | - |
|  | First-Level Surges | R4-12 [30] | ER | ER | ER |
|  | Warning | R4-13 [31] | ER | ER | ER |
| 4.6.9.1.1 | Equipment Ports With Secondary Protection | R4-14 [169] | ER | ER | TBD |
| 4.6.9.2 | Ports Connected to Shielded Cables | - | - | - | - |
|  | First-Level Surges | R4-15 [170] | ER | ER | TBD |
|  | Warning | R4-16 [171] | ER | ER | TBD |
| 4.6.10 | First-Level AC Power Fault Tests (Telecommunications Type 1,3, and 5 Port) | R4-17 [35] | ER | ER | ER |
| 4.6.10.1 | Equipment Ports With Secondary Protectors | - | - | - | - |
|  | Voltage Limiting | R4-18 [172] | ER | ER | TBD |
|  | Current Limiting | R4-19 [173] | ER | ER | TBD |
| 4.6.11 | Current-Limiting Protector Tests for Equipment To Be Located at Network Facilities (Type 1 Telecommunications Ports) | - | - | - | - |
|  | Equipment Requiring External Current- limiting Protectors | R4-20 [34] | ER | ER | ER |
|  | High-Speed Equipment Requiring Current-limiting Protectors | CR4-21 [135] | ER | ER | ER |
|  | High-Speed Equipment not Requiring Current-limiting Protectors | CO4-22 [136] | ER | ER | ER |
| 4.6.12 | Second-Level AC Power Fault Tests for Equipment To Be Located at Network Facilities (Type 1 Telecommunications Port) | R4-23 [36] | ER | ER | ER |
| 4.6.12.1 | Equipment Ports With Secondary Protection | - | - | - | - |
|  | Voltage Limiting | R4-24 [174] | ER | ER | TBD |
|  | Current Limiting | R4-25 [175] | ER | ER | TBD |
| 4.6.13 | Second-Level AC Power Fault Tests for Series-Type Equipment To Be Located at Network Facilities (Type 1 Telecommunications Port) | R4-26 [37] | ER | ER | ER |
| 4.6.14 | Fusing Coordination Tests for Equipment To Be Located on Customer Premises and OSP Facilities (Type 3 and 5 Telecommunications Ports) | R4-27 [39] | ER | ER | ER |
| 4.6.15 | Second-Level AC Power Fault Tests for Equipment To Be Located on Customer Premises and OSP Facilities (Type 3 and 5 Telecommunications Ports) | R4-28 [137] | ER | ER | ER |
| 4.6.15.1 | Equipment Ports With Secondary Protection | - | - | - | - |
|  | Voltage Limiting | R4-29 [176] | ER | ER | TBD |
|  | Current Limiting | R4-30 [177] | ER | ER | TBD |
| 4.6.15.2 | Tests for Ungrounded Exposed Conductive Surfaces |  |  |  |  |
|  | Dielectric Breakdown | R4-31 [138] | ER | ER | ER |
|  | Deleted | R4-32 [139] | - | - | - |
| 4.6.16 | Second-Level AC Power Fault Tests for Series-Type Equipment To Be Located on Customer Premises and OSP Facilities (Type 3 and 5 Telecommunications Ports) | R4-33 [140] | ER | ER | ER |
| 4.6.17 | Second-Level Intra-Building AC Power Fault Tests for Equipment To Be Located on Customer Premises (Type 4 Telecommunications Port) | - | - | - | - |
|  | Second-Level AC Power Fault | R4-34 [40] | ER | ER | ER |
|  | Ungrounded 15-minute Short Circuit Test | R4-35 [125] | ER | ER | ER |
|  | Grounded 15-minute Short Circuit Test | R4-36 [41] | ER | ER | ER |
| 4.7 | Lightning Protection Tests for Equipment To Be Located in High-Exposure Customer Premises and OSP Facilities (Type 3 and 5 Telecommunications Ports) | CO4-37 [178] | ER | ER | TBD |
| 4.8 | Criteria for Equipment interfacing With Agreed Primary Protection | - | - | - | - |
|  | Agreed Primary Protection | R4-38 [179] | ER | ER | TBD |
|  | Primary Protection Compliance | R4-39 [180] | ER | ER | TBD |
|  | Warning | R4-40 [181] | ER | ER | TBD |
| 4.9 | Criteria for Equipment With Integrated Primary Protection | R4-41 [182] | ER | ER | TBD |
| 4.9.1 | Equipment Classification | - | - | - | - |
|  | Warning | R4-42 [183] | ER | ER | TBD |
|  | EIPP Classification | R4-43 [184] | ER | ER | TBD |
| 4.9.2 | Protector Requirements | - | - | - | - |
|  | Protector Units Listed or Recognized | R4-44 [185] | ER | ER | TBD |
|  | EIPP Listed | R4-45 [186] | ER | ER | TBD |
|  | EIPP Classified | R4-46 [187] | ER | ER | TBD |
|  | EIPP Marked or Labeled | R4-47 [188] | ER | ER | TBD |
|  | Appropriate Equipment | R4-48 [189] | ER | ER | TBD |
|  | Documentation | R4-49 [190] | ER | ER | TBD |
| 4.9.3 | Lightning Surge and Power Fault Test for Protected Circuits | R4-50 [191] | ER | ER | TBD |
| 4.9.3.1 | Overcurrent Protection Coordination Test for Protected Circuits | R4-51 [192] | ER | ER | TBD |
| 4.9.4 | Fusing Coordination for Unprotected Circuits | - | - | - | - |
| 4.9.4.1.1 | Fusing Coordination Test for Circuits Suitable for Fusing | R4-52 [193] | ER | ER | TBD |
| 4.9.4.1.2 | Enclosure Suitable for Fusing | - | - | - | - |
|  | Made of Metal | R4-53 [194] | ER | ER | TBD |
|  | Polymeric Materials | R4-54 [195] | ER | ER | TBD |
|  | No Vents or Openings | R4-55 [196] | ER | ER | TBD |
|  | Seals and Gaskets (OSP Environment) | R4-56 [197] | ER | ER | TBD |
|  | 12-Gage Shotgun Blast | R4-57 [198] | ER | ER | TBD |
| 4.9.4.2 | Fusing coordination Test for Circuits Not Acting as Fuse Links | R4-59 [199] | ER | ER | TBD |
| 4.9.5 | Dielectric Withstand | R4-59 [200] | ER | ER | TBD |
| 4.9.6 | Stub Cable Requirements | - | - | - | - |
|  | Appropriate Cable Stub | R4-60 [201] | ER | ER | TBD |
|  | Cable Stub Requirements | R4-61 [202] | ER | ER | TBD |
| 4.9.7 | AC Power Fault Immunity | R4-62 [203] | ER | ER | TBD |
| 4.9.8 | Lightning Surge Tests | R4-63 [204] | ER | ER | TBD |
| 4.9.8.1 | Lightning Surge Test for Severe Climatic Conditions | - | - | - | - |
|  | No Damage | CR4-64 [205] | ER | ER | TBD |
|  | Fire, Fragmentation or Safety Hazard | CR4-65 [206] | ER | ER | TBD |
| 4.10 | Criteria for Equipment Interfacing with Coaxial Cable Ports | - | - | - | - |
|  | Need for an external protector | R4-66 [94] | ER | ER | ER |
|  | Section 4.10.2 and Section 4.10.3 Criteria | R4-67 [95] | ER | ER | ER |
|  | Section 4.10.4 Criteria | R4-68 [96] | ER | ER | ER |
|  | Section 4.10.2 and Section 4.10.3. Criteria for System Level Configuration. | CR4-69 [97] | ER | ER | ER |
| 4.10.2 | Short-Circuit Tests | R4-70 [99] | ER | ER | ER |
| 4.10.3 | Broadband Communications Equipment Intended for Use Without External Protectors | - | - | - | - |
|  | Internal Protectors | R4-71 [100] | ER | ER | ER |
|  | Internal Protector Access | R4-72 [101] | ER | ER | ER |
|  | Internal Protector Output Ports | CR4-73 [102] | ER | ER | ER |
| 4.10.3.1 | First-Level Lightning and Power Fault Tests | R4-74 [103] | ER | ER | ER |
| 4.10.3.2 | Second-Level Lightning and Power Fault Tests | - | - | - | - |
|  | Fire, Fragmentation or Safety Hazard | R4-75 [104] | ER | ER | ER |
|  | Customer Premises, CO’s or Headend | R4-76 [105] | ER | ER | ER |
|  | OSP | O4-77 [106] | ER | ER | ER |
|  | Documentation | R4-78 [107] | ER | ER | ER |
| 4.10.4 | Broadband Communications Equipment Intended for Use with an External Protector | - | - | - | - |
| 4.10.4.1 | First-Level Lightning and Power Fault Tests | R4-79 [108] | ER | ER | ER |
| 4.10.4.2 | Second-Level Lightning and Power Fault Tests | - | - | - | - |
|  | Fire, Fragmentation or Safety Hazard | R4-80 [109] | ER | ER | ER |
|  | Customer Premises, CO’s or Headend | R4-81 [110] | ER | ER | ER |
|  | OSP | O4-82 [111] | ER | ER | ER |
|  | Documentation | R4-83 [112] | ER | ER | ER |
| 4.10.5 | First-Level intrabuilding Surge Tests | - | - | - | - |
|  | No Damage | R4-84 [207] | ER | ER | TBD |
|  | Warning | R4-85 [208] | ER | ER | TBD |
| 4.10.6 | Additional criteria for Equipment Intended for the OSP | - | - | - | - |
|  | Power Fault | R4-86 [113] | ER | ER | ER |
|  | Surge | R4-87 [114] | ER | ER | ER |
| 4.11 | Lightning Criteria for Equipment interfacing With Antennas | R4-88 [209] | ER | ER | TBD |
| 4.12 | Lightning Criteria for Equipment Interfacing With AC Power Port(s) | R4-89 [210] | ER | ER | TBD |
| 4.12.1 | Equipment Used in Facilities With an External SPD | - | - | - | - |
|  | First-Level Surge | R4-90 [32] | ER | ER | ER |
|  | Second-Level Surge | R4-91 [33] | ER | ER | ER |
| 4.12.2 | Equipment Used in Facilities Without and External SPD | R4-92 [211] | ER | ER | TBD |
| 4.13 | Lightning Criteria for Equipment Interfacing With DC Power Port(s) | - | - | - | - |
| 4.13.1 | Test Directly on DC Power Port | O4-93 [212] | ER | ER | TBD |
| 5 | Steady-State Power Induction | - | - | - | - |
| 5.2 | Longitudinal Induction Criteria for Long (>20 kft) Loops | - | - | - | - |
| 5.2.4 | Performance Criteria | - | - | - | - |
|  | Requirement | R5-1 [42] | ER | ER | ER |
|  | Conditional Requirement | CR5-2 [43] | ER | ER | ER |
| 5.2.5 | Noise Performance for Voice band Circuits |  |  |  |  |
|  | Requirement | R5-3 [44] | ER | ER | ER |
|  | Conditional Requirement | CR5-4 [45] | ER | ER | ER |
| 5.3 | Longitudinal Induction Criteria for Short (<20 kft) Loops | - | - | - | - |
| 5.3.3.1 | Test Procedure for ISDN Technology | R5-5 [46] | ER | ER | ER |
| 5.3.4 | Performance Criteria | R5-6 [47] | ER | ER | ER |
| 5.3.5 | Noise Performance for Voice band Circuits | R5-7 [48] | ER | ER | ER |
| 5.4 | Longitudinal Induction Criteria for Analog Trunks | - | - | - | - |
| 5.4.4 | Performance Criteria |  |  |  |  |
|  | Requirement | R5-8 [49] | ER | ER | ER |
|  | Conditional Requirement | CR5-9 [50] | ER | ER | ER |
| 5.4.5 | Noise Performance for Voice band Circuits | - | - | - | - |
|  | Requirement | R5-10 [51] | ER | ER | ER |
|  | Conditional Requirement | CR5-11 {52] | ER | ER | ER |
| 5.5 | Longitudinal Induction Criteria for Coaxial Cables | - | - | - | - |
| 5.5.3 | Performance Criteria | - | - | - | - |
|  | Requirement | R5-12 [141] | ER | ER | ER |
|  | Conditional Requirement | O5-13 [142] | ER | ER | ER |
| 6 | DC Potential Difference | R6-1 [53] | ER | ER | ER |
| 7 | Electrical Safety Criteria | - | - | - | - |
| 7.2 | Listing Requirements | - | - | - | - |
|  | AC Powered Network Equipment | R7-1 [22] | ER | ER | ER |
|  | Convenience Receptacles | R7-2 [23] | ER | ER | ER |
|  | Customer Premises Equipment | R7-3 [24] | ER | ER | ER |
| 7.3 | Classification of Voltages | R7-4 [143] | ER | ER | ER |
| 7.3.1 | Continuous Voltage and Current Limits |  |  |  |  |
|  | Continuous Source | R7-5 [115] | ER | ER | ER |
|  | Ground Fault or Voltage Shutdown | R7-6 [144] | ER | ER | ER |
| 7.4 | Continuous Source Requirements | - | - | - | - |
| 7.4.1 | Class A1 Voltage Accessibility Requirements | R7-7 [54] | ER | ER | ER |
| 7.4.2 | Class A2 Voltage Accessibility Requirements | R7-8 [55] | ER | ER | ER |
| 7.4.3 | Class A3 Voltage Accessibility Requirements | - | - | - | - |
|  | Inaccessible | R7-9 [56] | ER | ER | ER |
|  | Insulation, Baffling, or Location | R7-10 [57] | ER | ER | ER |
|  | Labeled | R7-11 [58] | ER | ER | ER |
| 7.4.4 | Class AB Voltage Accessibility Requirements |  |  |  |  |
|  | OSP | R7-12 [59] | ER | ER | ER |
|  | Inaccessible | R7-13 [60] | ER | ER | ER |
|  | No Bare-Handed Contact | R7-14 [61] | ER | ER | ER |
|  | Labeled | R7-15 [62] | ER | ER | ER |
| 7.4.5 | Class B Voltage Accessibility Requirements | R7-16 [63] | ER | ER | ER |
| 7.5 | Duration-Limited Source Requirements | - | - | - | - |
| 7.5.1 | Interrupted/Tripped Sources |  |  |  |  |
|  | > 300V Peak-to-Peak | R7-17 [64] | ER | ER | ER |
|  | No Exceed Class A2 Voltage Limit | R7-18 [65] | ER | ER | ER |
|  | Series Current-Sensitive Tripping Device | R7-19 [66] | ER | ER | ER |
|  | NRTL Data | R7-20 [145] | ER | ER | ER |
| 7.5.2 | Transient Sources | R7-21 [67] | ER | ER | ER |
| 7.6 | Power Limitation Requirement | R7-22 [68] | ER | ER | ER |
| 7.7 | Leakage Currents from Exposed Surfaces | - | - | - | - |
| 7.7.2.1 | Leakage Current Requirements for Large Area Contact | R7-23 [69] | ER | ER | ER |
| 7.7.2.2 | Leakage Current Requirements for Small Area Contact | R7-24 [70] | ER | ER | ER |
| 7.7.2.3 | Leakage Current Between Surfaces of Equipment | R7-25 [71] | ER | ER | ER |
| 8 | Corrosion | - | - | - | - |
| 8.1 | Polarity of DC Voltages Applied to OSP Cabling | O8-1 [72] | ER | ER | ER |
| 8.2 | Magnitude of DC Voltages Applied to OSP Cabling | O8-2 [73] | ER | ER | ER |
| 9 | Bonding and Grounding | - | - | - | - |
| 9.2 | General Requirements Principles | - | - | - | - |
|  | Deleted | R9-1 [74] | - | - | - |
|  | Bonding Path Provided | R9-2 [75] | ER | ER | ER |
| 9.3 | Equipment Grounding Systems | R9-3 [76] | ER | ER | ER |
| 9.3.1 | Common Bonding Network (CBN) | R9-4 [116] | ER | ER | ER |
| 9.4 | AC Equipment Grounding | R9-5 [77] | ER | ER | ER |
| 9.5 | Communication Equipment Grounding | R9-6 [213] | ER | ER | TBD |
| 9.5.1 | Network Telecommunications Facilities | R9-7 [78] | ER | ER | ER |
| 9.5.2 | Locations Where the NEC Applies | R9-8 [146] | ER | ER | ER |
| 9.5.3 | Outside Plant | R9-9 [147] | ER | ER | ER |
| 9.6 | Equipment Unit Bonding and Grounding | R9-10 [79] | ER | ER | ER |
| 9.7 | Provisions for Unit Assembly Bonding and Grounding | R9-11 [148] | ER | ER | ER |
| 9.7.1 | Connectors and Connection Methods for Equipment Unit Assemblies | R9-12 [149] | ER | ER | ER |
| 9.7.2 | Bonding of Circuit Packs | R9-13 [150] | ER | ER | ER |
| 9.8 | DC Power System Grounding | - | - | - | - |
| 9.8.1 | Centralized Power Sources | R9-14 [80] | ER | ER | ER |
| 9.8.2 | Embedded Power Sources | R9-15 [81] | ER | ER | ER |
| 9.8.3 | Bonding of Battery Return (BR) Input Terminals | - | - | - | - |
|  | Documentation | R9-16 [151] | ER | ER | ER |
|  | Conductor Ampacity | R9-17 [152] | ER | ER | ER |
| 9.9 | Bonding and Grounding Conductor and Connection Requirements | - | - | - | - |
| 9.9.1 | Bonding and Grounding Conductors | R9-18 [82] | ER | ER | ER |
| 9.9.2 | Connections | - | - | - | - |
|  | Suitable Materials | R9-19 [83] | ER | ER | ER |
|  | Bare Conductors | R9-20 [84] | ER | ER | ER |
|  | Multiple Connectors | R9-21 [85] | ER | ER | ER |
|  | Unplated Connectors | R9-22 [86] | ER | ER | ER |
|  | Listed Fastening Hardware | R9-23 [87] | ER | ER | ER |
|  | Nonconductive Coatings | R9-24 [88] | ER | ER | ER |
| 9.9.3 | Connectors | - | - | - | - |
|  | Listed | R9-25 [89] | ER | ER | ER |
|  | Grounding and Bonding Conductors | R9-26 [90] | ER | ER | ER |
|  | Conductor Termination | R9-27 [91] | ER | ER | ER |
| 9.10 | Short Circuit Tests | - | - | - | - |
| 9.10.1 | DC Power Sources | R9-28 [92] | ER | ER | ER |
| 9.10.2 | AC Power Sources | R9-29 [93] | ER | ER | ER |
| 9.12 | Compatibility of Former IBN Equipment with CBN Currents | - | - | - | - |
| 9.12.1.7 | Test Environment | CR9-30 [117] | ER | ER | ER |
| 9.12.2 | Identification of Test Points | R9-31 [118] | ER | ER | ER |
| 9.12.3 | DC Fault Test | CR9-32 [119] | ER | ER | ER |
| 9.12.4 | Frame EFT Test | CR9-33 [121] | ER | ER | ER |
| 9.12.5 | Frame Surge Test | - | - | - | - |
|  | 3000A, 8/20-µs current surge | CR9-34 [122] | ER | ER | ER |
|  | 5000A, 8/20-µs current surge | CO9-35 [123] | ER | ER | ER |
| 9.12.6 | AC Fault Test | CR9-36 [120] | ER | ER | ER |
| 9.13 | Grounding connector for Equipment With Integrated Primary Protection | - | - | - | - |
|  | Common Bonding Point | R9-37 [214] | ER | ER | ER |
|  | 60-Hz, 1500A for 6 Seconds | R9-38 [215] | ER | ER | ER |
| 9.13.1 | Grounding Conductors in the EIPP | - | - | - | - |
|  | Unless Fusing on the EUT Board | R9-39 [216] | ER | ER | TBD |
|  | If Fusing on the EUT Board | R9-40 [217] | ER | ER | TBD |
| 10 | Criteria for DC Power Port of Telecommunications Load Equipment | - | - | - | - |
| 10.1 | Input DC Voltage | R10-1 [218] | ER | ER | TBD |
| 10.2 | Minimum Operating Voltage | R10-2 [19] | ER | ER | TBD |
| 10.3 | Undervoltage Transient | - | - | - | - |
|  | Undervoltage with Redundant Power Feeds Disabled | R10-3 [220] | ER | ER | TBD |
|  | Undervoltage | R10-4 [221] | ER | ER | TBD |
| 10.4 | Overvoltage Transient | R10-5 [222] | ER | ER | TBD |
| 10.5 | Impulse Transient | R10-6 [223] | ER | ER | TBD |
| 10.6 | Single Transient | RO10-7 [224] | ER | ER | TBD |
| 10.7 | Noise Returned by the Network Equipment (Noise Emission) | - | - | - | - |
| 10.7.1 | Voice Frequency Noise Emission | R10-8 [225] | ER | ER | TBD |
| 10.7.2 | Wideband Frequency Noise Emission | R10-9 [226] | ER | ER | TBD |
| 10.7.3 | Broadband Noise Emission | R10-10 [227] | ER | ER | TBD |
| 10.8 | Power Input Noise Immunity | - | - | - | - |
| 10.8.1 | Voice Frequency Noise Immunity | R10-11 [228] | ER | ER | TBD |
| 10.8.2 | Wideband Frequency Noise Immunity | R10-12 [229] | ER | ER | TBD |
| 10.8.3 | Broadband Noise Immunity | R10-13 [230] | ER | ER | TBD |

C:  ANSI T1.307 – 2003

| Section | Section Name | Criteria | Verizon | AT&T | Qwest |
| --- | --- | --- | --- | --- | --- |
| 4 | Fire Resistance Requirements | - | - | - | - |
| 4.1 | Ignitability Requirements-Equip. Assemblies | R | ER | ER | ER |
| 4.2 | Fire Spread Requirements for Wire & Cable | R | ER | ER | ER |
| 4.3 | Fire Spread Requirements for Optical Cable Trays or Raceways | R | ER | ER | ER |
| 4.4 | Ignitability Requirements for Ancillary Materials | R | ER | ER | ER |
| 5 | Needle Flame Test Methods & Criteria | - | - | - | - |
| 5.1 | Needle Flame Test for Discreet Components | R | ER | ER | ER |
| 5.2 | Needle Flame Test for Components Mounted on Subassemblies | R | ER | ER | ER |

D:  ANSI T1.315 – 2001

| Section | Section Name | Criteria | Verizon | AT&T | Qwest |
| --- | --- | --- | --- | --- | --- |
| 5 | Telecommunications Load Equipment Performance Requirements | - | - | - | - |
| 5.1 | Steady-state input DC voltage requirements | R | ER | ER | ER |
| 5.1.1 | Distribution voltage drops | R | ER | ER | ER |
| 5.2 | Under voltage requirements | R | ER | ER | ER |
| 5.3 | Over voltage transient requirement | R | ER | ER | ER |
| 5.4 | Protective device operation transient | R | ER | ER | ER |
| 5.5.1 | Noise immunity | R | ER | ER | ER |

E:  ANSI T1.319 - 2002

| Section | Section Name | Criteria | Verizon | AT&T | Qwest |
| --- | --- | --- | --- | --- | --- |
| 4 | Fire Propagation Hazard Objectives | - | - | - | - |
| 4.1 | General | R | EC | ER | ER |
| 4.2 | Materials, Components, cables & wires | R | EC | ER | ER |
| 4.3 | Constructional Assessment Criteria | R | EC | ER | ER |
| 4.4 | Equipment Subjected to Fire Propagation Test | R | EC | ER | ER |
| 5 | Fire Propagation Hazard Test Apparatus and Calibration | - | - | - | - |
| 5.1 | Test Apparatus | R | EC | ER | ER |
| 5.2 | Calibration of Equipment | R | EC | ER | ER |
| 6 | Test Setups | - | - | - | - |
| 6.1 | Frame Level Equipment Tests | R | EC | ER | ER |
| 6.2 | Shelf Level Equipment Tests | R | EC | ER | ER |
| 6.3 | Sub-Assembly Tests | R | EC | ER | ER |
| 7 | Test Specimens | - | - | - | - |
| 7.1 | General | - | - | - | - |
| 7.2 | Conditioning | R | EC | ER | ER |
| 8 | Test Procedure | - | - | - | - |
| 8.1 | Preparation | R | EC | ER | ER |
| 8.2 | Procedure | R | EC | ER | ER |
| 9 | Calculations | - | - | - | - |

F:  ANSI T1.336 – 2003

| Section | Section Name | Criteria | Verizon | AT&T | Qwest |
| --- | --- | --- | --- | --- | --- |
| 4 | Performance Requirements | - | - | - | - |
| 4.1.1 | Lable | R | ER | ER | TBD |
| 4.1.1.1 | Test Procedure | R | ER | ER | TBD |
| 4.1.2 | Test Criteria | R | ER | ER | TBD |
| 4.2 | Static tests | - | - | - | - |
| 4.2.1 | Test Procedure | R | ER | ER | TBD |
| 4.2.2 | Preparation | R | ER | ER | TBD |
| 4.2.3 | Test Criteria | R | ER | ER | TBD |
| 4.2.5 | Documentation | R | ER | ER | TBD |
| 4.3 | Dynamic Test | - | - | - | - |
| 4.3.1 | Testing of Unequipped Framework | O | ER | ER | TBD |
| 5 | Physical Requirements | - | - | - | - |
| 5.1 | General Requirements | - | - | - | - |
| 5.1.1 | Construction Requirements | R | ER | ER | TBD |
| 5.1.2 | Construction Objectives | O | ER | ER | TBD |
| 5.1.3 | Side by Side Installations | R | ER | ER | TBD |
| 5.1.4 | Horizontal Requirements | R | ER | ER | TBD |
| 5.1.5 | Leveling Requirements | R | ER | ER | TBD |
| 5.1.6 | Frame Joint Design Requirements | R | ER | ER | TBD |
| 5.1.7 | Freestanding Installation | R | ER | ER | TBD |
| 5.2 | Fire Resistance | - | - | - | - |
| 5.2.1 | ANSI T1.307-2003 Compliance | R | ER | ER | TBD |
| 5.3 | Finish | - | - | - | - |
| 5.3.1 | Must Prevent Oxidation | R | ER | ER | TBD |
| 5.4 | Heat Dissipation | - | - | - | - |
| 5.4.1 | Free Airflow Path | R | ER | ER | TBD |
| 5.4.2 | Side Panels and Doors | R | ER | ER | TBD |
| 5.4.3 | Thermal Management | O | ER | ENR | TBD |
| 5.4.4 | Dimensional Requirements | R | ER | ER | TBD |
| 5.5 | Raised Floor System Configurations | - | - | - | - |
| 5.5.1 | Raised Floor Requirements | R | ER | ER | TBD |
| 5.6 | Geometric Dimensions | - | - | - | - |
| 5.6.1 | Outer Modular Dimension Requirements | R | ER | ER | TBD |
| 5.6.2 | Outer Modular Dimension Objective | O | ER | ER | TBD |
| 5.6.3 | Height Dimension | - | - | - | - |
| 5.6.3.1 | Baseline Height Dimension Requirement | R | ER | ER | TBD |
| 5.6.3.2 | Measurement Specifications | R | ER | ER | TBD |
| 5.6.3.3 | Compensation Requirement | R | ER | ER | TBD |
| 5.6.3.4 | Interface Objective | O | ER | ER | TBD |
| 5.6.4 | Depth Dimension | - | - | - | - |
| 5.6.4.1 | Depth Dimension Requirement | R | ER | ER | TBD |
| 5.6.4.2 | Baseline Depth Requirement | R | ER | ER | TBD |
| 5.6.4.3 | Alternative Depth Objective | O | ER | ER | TBD |
| 5.6.4.4 | Measurement Specifications | R | ER | ER | TBD |
| 5.6.4.5 | Open Doors Requirement | R | ER | ER | TBD |
| 5.6.4.6 | Reserved Space Objective | R | ER | ER | TBD |
| 5.6.4.7 | Design Requirements | R | ER | ER | TBD |
| 5.6.4.8 | Frame Depth Objective | O | ER | ENR | TBD |
| 5.6.5 | Width Dimension | - | - | - | - |
| 5.6.5.1 | Width Dimension Objective | O | ER | ER | TBD |
| 5.6.5.2 | Cable Management Objective | O | ER | ER | TBD |
| 5.6.5.3 | Alternative Width Objective | O | ER | ER | TBD |
| 5.6.5.4 | Side-To-Side Clearance | R | ER | ER | TBD |
| 5.6.5.5 | Width Dimension Requirements | R | ER | ER | TBD |
| 5.6.6 | Inside Dimensions | - | - | - | - |
| 5.6.6.1 | 23-Inch Shelf Mounting Objective | O | ER | ER | TBD |
| 5.6.6.2 | 19-Inch Shelf Mounting Objective | O | ER | ER | TBD |
| 5.6.6.3 | Vertical Aperture Requirement | R | ER | ER | TBD |
| 5.6.6.4 | Base Height Requirement | R | ER | ER | TBD |
| 5.6.6.5 | Maximum Height Requirement | R | ER | ER | TBD |
| 5.6.6.6 | Mounting Hole Requirement | R | ER | ER | TBD |
| 5.6.6.7 | Nominal Width Requirement | R | ER | ER | TBD |
| 5.6.6.8 | Mounting Centers Width Requirement | R | ER | ER | TBD |
| 5.6.6.9 | Mounting Pitch Requirement | R | ER | ER | TBD |
| 5.6.6.10 | Attachment Requirements | R | ER | ER | TBD |
| 5.6.6.11 | Setback Requirements | R | ER | ER | TBD |
| 5.7 | Junction Details | - | - | - | - |
| 5.7.1.1 | Alignment Requirements | R | ER | ER | TBD |
| 5.7.1.2 | Earthquake Resistance Objective | O | ER | ER | TBD |
| 5.7.1.2 | Junction Location Requirements | R | ER | ER | TBD |
| 5.7.1.4 | Hole Requirements | R | ER | ER | TBD |
| 5.7.1.5 | Spacer and Hardware Requirement | R | ER | ER | TBD |
| 5.7.1.6 | Removal and Installation Requirement | R | ER | ER | TBD |
| 5.7.2 | End Guards | - | - | - | - |
| 5.7.2.1 | End Guard Requirements | R | ER | ER | TBD |
| 5.7.2.1.1 | Top Mounting Hole Requirements | R | ER | ER | TBD |
| 5.7.2.1.2 | Bottom Mounting Hole Requirements | R | ER | ER | TBD |
| 5.7.3 | Anchoring To A Floor | - | - | - | - |
| 5.7.3.1 | Minimum of Four Mounting Holes | R | ER | ER | TBD |
| 5.7.3.2 | Lateral Relocation Requirement | R | ER | ER | TBD |
| 5.7.3.3 | Fastener Location Requirements | R | ER | ER | TBD |
| 5.7.3.4 | Anchor Accessibility Requirement | R | ER | ER | TBD |
| 5.7.3.5 | Existing cable Line-up | R | ER | ER | TBD |
| 5.7.3.6 | Self-Supporting Requirements | R | ER | ER | TBD |
| 5.7.3.7 | Structural Spacer Objective | O | ER | ER | TBD |
| 5.7.4 | Leveling Devices | - | - | - | - |
| 5.7.4.1 | Leveling Device Requirements | R | ER | ER | TBD |
| 5.7.5 | Lifting Points | - | - | - | - |
| 5.7.5.1 | Quantity and Loading Requirements | R | ER | ER | TBD |
| 5.7.5.2 | Lifting Point Positioning | R | ER | ER | TBD |
| 5.7.6 | Grounding | - | - | - | - |
| 5.7.6.1 | Grounding per ANSI T1.333.2001 | R | ER | ER | TBD |
| 5.7.6.2 | Reference T1.333-2001 | O | ER | ER | TBD |
| 5.7.6.3 | Equipment Ground Requirements | R | ER | ER | TBD |
| 5.7.7 | Isolation | - | - | - | - |
| 5.7.7.1 | Isolation Requirements | R | ER | ER | TBD |
| 5.7.8 | ESD/Jack, Location | - | - | - | - |
| 5.7.8.1 | ESD Protection Provided | R | ER | ER | TBD |
| 5.7.8.2 | ESD Jacks Front and Rear of Frame | R | ER | ER | TBD |
| 5.7.8.3 | ESD Jacks Locations (specific) | R | ER | ER | TBD |
| 5.7.9 | Aisle Spacing | - | - | - | - |
| 5.7.9.1 | Aisle Dimension Objective | O | ER | ENR | TBD |
| 6 | Cable Areas | - | - | - | - |
| 6.1 | Cable Access | - | - | - | - |
| 6.1.1 | Top and Bottom Cable Access | R | ER | ER | TBD |
| 6.1.2 | Side to Side Cable Access | O | ER | ER | TBD |
| 6.1.3 | Cable Shall Not Extend Beyond the Edges of the Frame | R | ER | ER | TBD |
| 6.2 | Equipment Frame Interface With Cable Rack | - | - | - | - |
| 6.2.1 | Distribution System Provisions | R | ER | ER | TBD |
| 6.2.1.1 | Allow Removal and Insertion | R | ER | ER | TBD |
| 6.2.1.2 | Top Cross Member Fastening | O | ER | ER | TBD |
| 6.2.1.3 | Overhead Cable Provisions | R | ER | ER | TBD |
| 6.3 | UTF Cable Distribution Under Raised Floor | - | - | - | - |
| 6.3.1 | Under Floor Installation | R | ER | ER | TBD |
| 6.3.1.1 | Under Floor Feeder Rack Objective | O | ER | ER | TBD |
| 6.3.1.2 | Cable Support Objective | O | ER | ER | TBD |
| 6.3.2 | Cable Segregation Objective | O | ER | ER | TBD |
| 6.3.3 | Location of Cable Entry (Access Floor) | - | - | - | - |
| 6.3.3.1 | Cable Entry Location | R | ER | ER | TBD |
| 6.4 | AC Convenience Outlet | - | - | - | - |
| 6.4.1 | AC Power placement | R | ER | ER | TBD |
| 6.4.2 | Conduit Spacing Provisions | R | ER | ER | TBD |
| 6.4.3 | Conduit Pass Through Provisions | R | ER | ER | TBD |
| 6.4.4 | NEC Compliance | O | ER | ER | TBD |
| 6.4.5 | Convenience Outlet Alternate Location | O | ER | ER | TBD |
| 7 | Air Path | - | - | - | - |
| 7.1 | Under Floor Air Entry | - | - | - | - |
| 7.1.1 | Under Floor Plenum | O | ER | ER | TBD |
| 7.1.2 | Front Panel | O | ER | ER | TBD |
| 8 | Accessories | - | - | - | - |
| 8.1 | UTF Door And Side Panels | - | - | - | - |
| 8.1.1 | Door Panel Thickness | R | ER | ER | TBD |
| 8.1.2 | Open Door | R | ER | ER | TBD |
| 8.1.3 | Bonding Straps | R | ER | ER | TBD |
| 8.1.4 | Depth Dimension | R | ER | ER | TBD |
| 8.1.5 | Open/Close Frame Configuration | O | ER | ER | TBD |
| 8.1.6 | Metallic Construction | O | ER | ER | TBD |
| 8.1.7 | Reversible | O | ER | ER | TBD |
| 8.1.8 | Venting Requirements | O | ER | ER | TBD |
| 8.1.9 | Solid Panel Dimensions | O | ER | ER | TBD |
| 8.2 | Anchor Kits | - | - | - | - |
| 8.2.1 | Availability | O | ER | ER | TBD |
| 8.2.2 | Include Required Hardware | O | ER | ER | TBD |
| 8.3 | End Guards | - | - | - | - |
| 8.3.1 | Minimum Width | O | ER | ER | TBD |
| 8.3.2 | Depth and Height | O | ER | ER | TBD |
| 8.3.3 | Fastening Details | O | ER | ER | TBD |
| 8.4 | Junction Kits | - | - | - | - |
| 8.4.1 | Design | O | ER | ER | TBD |
| 8.4.2 | Hardware Provided | O | ER | ER | TBD |
| 8.5 | Cable Management Spacers | - | - | - | - |
| 8.5.1 | Alternative Width | O | ER | ER | TBD |
| 8.5.2 | Dimension Specifics | O | ER | ER | TBD |
| 8.5.3 | Fastening Details | O | ER | ER | TBD |
| 8.6 | Isolation Materials | - | - | - | - |
| 8.6.1 | Non-conductive Materials | O | ER | ER | TBD |
| 8.6.2 | Isolation Pads | O | ER | ER | TBD |
| 8.7 | Extenders | - | - | - | - |
| 8.7.1 | Height Extenders | O | ER | ER | TBD |
| 8.7.2 | Extender Dimensions | O | ER | ER | TBD |
| 8.8 | UTF Transport Systems (FTS) | - | - | - | - |
| 8.8.1 | Availability | O | ER | ER | TBD |

###### Test Report Certification

A completed copy of this certification must be attached to each test report.  The carrier will not accept test reports without accurate and complete certifications.  Please direct any questions to the carrier’s NEBS compliance contact.

| Report Number | Name of Test Lab | Address of Test Lab | Report Date |
| --- | --- | --- | --- |

| Test Description | Name of Test Lab | Address of Test Lab | Date of test |
| --- | --- | --- | --- |

Independent Test Laboratory Director:  I hereby certify that the NEBS testing described in the indicated report was performed according to the NEBS requirements listed in the Telecommunications Carrier NEBS Checklist and the applicable ANSI and Telcordia NEBS Generic Requirements.  I also certify that the testing was performed at the laboratory locations, dates and times listed above.

| Signature, Title, Organization | Date |
| --- | --- |

Manufacturer’s Test Laboratory Director:  I hereby certify that the NEBS testing described in the indicated report has been performed according to the NEBS requirements listed in the Telecommunications Carrier NEBS Checklist and the applicable ANSI and Telcordia NEBS Generic Requirements.  I also certify that the testing was performed at the laboratory locations, dates and times listed above.

| Signature, Title, Organization | Date |
| --- | --- |

###### NEBS Compliance Checklist

(All applicable information must be provided to avoid evaluation delays.

Please direct any questions of applicability to the carrier’s NEBS compliance contact.)

A.  GENERAL INFORMATION   (Required for CLEC & Carrier Applications.)

| 1Date: |  | (Initial) |  |  | 2Date: |  | (Revised, All changes shall be clearly highlighted or identified) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2Supplier Name: |  |  |  |  |  |  |  |  |  |
| 3Supplier Contact: |  |  |  |  |  |  |  | 4Phone #: |  |
| 5Supplier e-mail address: |  |  |  |  |  |  |  | 6FAX #: |  |
| 7Equipment type/name: |  |  |  |  |  |  |  |  |  |
| 8System/Model Number: |  |  |  |  |  |  |  |  |  |
| 9Detailed Configuration Information: |  |  |  |  |  |  |  |  |  |

If equipment has optional configurations, modules, plug-in cards or circuit packs, a complete listing of modules/units must be included – please clearly show unit names, model numbers and plug-in card relationships. Attach lists and sketches of tested hardware units showing specific module locations, to this checklist. Complete the table below (items 15, 16 and 17) as required. Duplicate or repeat the table or lines as necessary.

| 10Shelf description: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Manufacturer: | Model Name/Number: |  |  | Part Number: |
| 11Plug-in card or module descriptions for above shelf (List only one of each type:) |  |  |  |  |
| Model/Name: |  |  | Part Number: |  |
| 12Remarks for above shelf or plug-ins: |  |  |  |  |

| 13Carrier use (Yes/No): |  |  | 14Collocator use (Name): |  |
| --- | --- | --- | --- | --- |
| 15Project/Application description: Specify Function, Customer Premises, Host/Remote, COT/RT, number of sites, specific States/Cities, Carrier wide, etc.: |  |  |  |  |

B.  POWER REQUIREMENTS   (Required for CLEC & Carrier Applications.  All items must be answered – Do not change any measurement units)

| 1-48v DC (Carrier Preferred): |  | Yes |  | No |  |  | Amps |  |  |  |  |  | Watts |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2Alternate/Additional Requirements: |  |  |  |  |  |  | Amps |  |  |  |  |  | Watts |  |  |  |  |  |  |  |  |
| 3Peripheral Equipment Requirements: |  |  |  |  |  |  | Amps |  |  |  |  |  | Watts |  |  |  |  |  |  |  |  |
| 4Power Drain: |  |  |  |  |  |  | List 1 |  |  |  |  |  | List 2 |  |  |  |  |  |  |  |  |
| 5Return Current Architecture Equipment Requirements: |  |  |  |  |  |  | DC-I |  |  |  |  |  | DC-C |  |  |  |  |  |  |  |  |
| 6Is AC power mandatory for any system component: |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  |  |  | No |  |  |
| 7Is this power information representative of a specific, typical or maximum configuration? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 8List equipment voltage classification(s) per GR-1089, Section 7.3: |  |  |  |  |  |  |  | Class: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9Comments/Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

C.  GROUNDING REQUIREMENTS    (Required for CLEC & Carrier Applications.  Refer to TR-NWT-000295; this is not the same as UL 1950.  All items must be answered)

| 1 Does this equipment conform to the Integrated Ground Plane requirements in GR-1089 Section 9? |  |  | Yes |  |  | No |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2Is this equipment compatible with the TR-NWT-000295 for Isolated Ground Plane? |  |  | Yes |  |  | No |  |  |
| 3Is internal logic ground isolated from chassis/framework ground? |  |  | Yes |  |  | No |  |  |
| 4Is signal ground, external interface, isolated from chassis/framework ground? |  |  | Yes |  |  | No |  |  |
| 5Is chassis/framework used as a current carrying conductor? |  |  | Yes |  |  | No |  |  |
| 6Comments/Describe: |  |  |  |  |  |  |  |  |

D.  PHYSICAL SIZE/MOUNTING REQUIREMENTS    (Required for CLEC & Carrier Applications.  All items must be answered – Do not change any measurement units)

| 1 Is equipment a circuit pack, shelf, frame, rack, cabinet or multiple frames? Explain if required. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2 Does equipment mount on a relay rack or cabinet included as part of system? |  |  | Yes |  |  | No |  |  |
| 3 Does cabinet or equipment unit/mounting have doors or removable covers on front? |  |  | Yes |  |  | No |  |  |
| 4 Does cabinet or equipment unit/mounting have doors or removable covers on rear? |  |  | Yes |  |  | No |  |  |
| 5 Is access to rear of relay rack/cabinet required for maintenance? |  |  | Yes |  |  | No |  |  |
| 6 Is metallic cabling terminated on the rear of equipment? |  |  | Yes |  |  | No |  |  |
| 7 Are fiber cables and test access points terminated on the front of equipment? |  |  | Yes |  |  | No |  |  |
| 8 Does the equipment include cable guards/strain relief? |  |  | Yes |  |  | No |  |  |
| 9 Does the equipment automatically reduce power to open fiber ports? |  |  | Yes |  |  | No |  |  |
| 10 Do fiber ports point downward? |  |  | Yes |  |  | No |  |  |
| 11Is equipment installed exclusively indoors in a CO, CEV, HUT, or customers’ Premises? |  |  | Yes |  |  | No |  |  |
| 12 Is Equipment installed exclusively outdoors in a metal enclosure? |  |  | Yes |  |  | No |  |  |
| 13 Equipment dimensions measured in normal mounting configuration. |  | Height |  |  |  |  | Inches |  |
|  |  | Width |  |  |  |  | Inches |  |
|  |  | Depth |  |  |  |  | Inches |  |
| 14 Minimum aisle clearance required for fully open door ‘clear swing’ – front. |  |  |  |  |  |  | Inches |  |
| 15 Minimum aisle clearance required for fully open door ‘clear swing’ – rear. |  |  |  |  |  |  | Inches |  |
| 16 Equipment total weight. |  |  |  |  |  |  | Lbs. |  |
| 17 Comments: |  |  |  |  |  |  |  |  |

E.  HEAT RELEASE DATA  (Required for CLEC & Carrier Applications.)

| 1 Is equipment forced air-cooled by its own fan unit? |  | Yes |  |  | No |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 2 Does the equipment use replaceable air filters? (Check carriers for specific requirements). |  | Yes |  |  | No |  |  |
| 3 Does heat release vary with traffic load? |  | Yes |  |  | No |  |  |
| 4 Describe product airflow, intake to exhaust. (i.e. bottom front to top rear) |  |  |  |  |  |  |  |
| 5 Is heat release calculated for a specified traffic level? |  | Yes |  |  | No |  |  |
| 6 If yes, specify the traffic level used in the calculated heat release. |  |  |  |  |  | CCS |  |
| 7 Maximum Aisle Facing Surface Temperature (GR-63: O4-15). |  |  |  |  |  | oF |  |

| List each active component in system: |  | No. Units to be Used in System1 |  | Heat Dissipation per Unit/Traffic %2 |  | Heat Dissipation per total sub-system3 |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ## Description/Card Number | Part Number | A: Max Possible: | B: This System: | C: Max % Traffic : | D: This System: | Watts Max A x C | Watts this System B x D |
| Total Watts for System: |  |  |  |  |  |  |  |

Notes:

- Max Poss:  The maximum number of units of this component that can be used in the system as designed

This System:  The maximum number of units of this component per planned deployment

2     Max %:  Heat dissipation for a unit in watts, when operating at maximum capacity

This System:  Heat dissipation for a unit in watts, when operating at maximum capacity expected for deployment

3	Watts Max:  Maximum number of units times maximum heat dissipation per unit

Watts This System:  Maximum number of units for this system times estimated heat dissipation per unit under maximum capacity when deployed

F.  ALARM AND PERFORMANCE MONITORING INTERFACE

| 1 Do all fuse alarms provide audible, visual, local, and remote reporting? |  |  |  |  |  | Yes |  |  | No |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2 Does equipment include a provision for connection to local/remote external alarms and/or performance monitoring systems? |  |  |  |  |  | Yes |  |  | No |  |  |
| 3 Can alarms be transmitted to remote locations? |  |  |  |  |  | Yes |  |  | No |  |  |
| 4 Can alarms be retired from remote locations? |  |  |  |  |  | Yes |  |  | No |  |  |
| 5 Can alarms be ‘obscured’ by other (e.g., lower level) alarms? |  |  |  |  |  | Yes |  |  | No |  |  |
| 6 Does equipment interface require proprietary Operational Support Systems? |  |  |  |  |  | Yes |  |  | No |  |  |
| 7 Identify/Describe proprietary Operational Support Systems: |  |  |  |  |  |  |  |  |  |  |  |
| 8 Specify supported performance-monitoring interfaces. TNM/NFM, NMA, TONICS, SNMP, TL1, CORBA, others? |  |  |  |  |  |  |  |  |  |  |  |
| 9 Additional Comments or Descriptions: |  |  |  |  |  |  |  |  |  |  |  |

G. GR-78 PHYSICAL DESIGN REQUIREMENTS   (Required for Carrier Applications, All items must be answered.  See Section 3.8.)

| GR-78 Section | # Element Requirement Description | Compliant |  |  |  |  | # Exceptions and Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3 | # Materials and Finishes Requirements |  |  |  |  |  |  |
| 3.1 | General: R3-4, R3-7 | Yes |  | No |  |  |  |
| 3.2.2 | Fire Risk Analysis: R3-10, R3-11 (Component Rating UL94, V-0 or V1), R3-12 | Yes |  | No |  |  |  |
| 3.2.3&3.2.4 | Fluxes: R3-14 / Silver - CR3-15 | Yes |  | No |  |  |  |
| 3.2.5 | Silicones: R3-16 | Yes |  | No |  |  |  |
| 3.3 | Finishes: R3-17-R3-20 (min 2% lead)-R3-23 | Yes |  | No |  |  |  |
| 4 | # Separable Connector Requirements |  |  |  |  |  |  |
| 4.1.1 | Design: Similar Metals: R4-1 through R4-20 | Yes |  | No |  |  |  |
| 4.1.2 | Noble Metallization: R4-21, R4-24 through 31 | Yes |  | No |  |  |  |
| 4.1.3 | Base metallization: R4-32 through R4-34 | Yes |  | No |  |  |  |
| 4.1.4 | Lubrication (Contacts): R4-35 through R4-40 | Yes |  | No |  |  |  |
| 4.3 | Component Sockets: R4-66 | Yes |  | No |  |  |  |
| 4.4 | Insulation Displacement Connect. R4-69 | Yes |  | No |  |  |  |
| 4.5 | Zero Insertion Force Connectors: R4-72 | Yes |  | No |  |  |  |
| 4.6 | Coaxial Connectors: R4-75 | Yes |  | No |  |  |  |
| 4.7 | Optical Connectors: R4-76 & 77 | Yes |  | No |  |  |  |
| 6. | # Printed Wiring Board Requirements |  |  |  |  |  |  |
| 6.1 | General: R6-1 | Yes |  | No |  |  |  |
| 6.1.1 | Materials: Laminates - R6-2 & 3; Solder Mask - R6-4 & 5; Repair Polymers - R6-7 | Yes |  | No |  |  |  |
| 6.1.2 | Design: Interlayer Connection - R6-16 & 17; Warpage - R6-19; Protect Coating - R6-21; Resistance to Airborne Contaminant - R6-22 | Yes |  | No |  |  |  |
| 6.1.3.2 | Conductor Widths & Spacing: R6-26 through 32 | Yes |  | No |  |  |  |
| 6.1.3.3 | Conductor Adhesion: R6-33 | Yes |  | No |  |  |  |
| 6.1.3.6 | Solder ability: R6-49 | Yes |  | No |  |  |  |
| 6.1.3.7 | Solder Masks: R6-50 through R6-64 | Yes |  | No |  |  |  |
| 6.1.3.9 | Insulation Resistance Testing: R6-78 through 84 | Yes |  | No |  |  |  |
| 6.1.3.10 | Solvent Extract Conductivity: R6-85 through 93 | Yes |  | No |  |  |  |
| 6.1.3.11 | Mechanical Damage: R6-95 through 108 | Yes |  | No |  |  |  |
| 6.1.3.14 | Repairs: R6-122 through 133 | Yes |  | No |  |  |  |
| 6.2 | Multi-layer PWBs - General Requirement |  |  |  |  |  |  |
| 6.2.1.1 | Dimensioning: R6-165 through R6-174 | Yes |  | No |  |  |  |
| 6.2.1.3 | Construction: R6-175 through R6-180 | Yes |  | No |  |  |  |
| 6.2.2.3 | Plated-Through Holes: R6-183 through 188 | Yes |  | No |  |  |  |
| 6.2.2.5 | Insulation Resistance Testing: R6-192 | Yes |  | No |  |  |  |
| 6.2.2.6 | Solvent Extract Conductivity (SEC) Testing: R6-193 through 196 | Yes |  | No |  |  |  |
| 6.2.2.10 | Repairs: Finished Multi-layer PWBs – R6-208 through 209 | Yes |  | No |  |  |  |
| 6.3 | # PWBs for Surface Mounting |  |  |  |  |  |  |
| 6.3.1.1 | Materials: laminates - 6-214 | Yes |  | No |  |  |  |
| 6.3.1.2 | Materials: solder masks - R6-215 | Yes |  | No |  |  |  |
| 6.3.1.3 | Component mounting pads: R6-216 through 218 | Yes |  | No |  |  |  |
| 6.3.1.4 | Design: solder masks - IP6-222 | Yes |  | No |  |  |  |
| 6.3.1.6 | PWBs for adhesive and wave solder, Soldering – Component Mounting Pads | Yes |  | No |  |  |  |
| 6.3.1.7 | PWBs for re-flow surface mounting soldering: Conductor finish: R6-228 | Yes |  | No |  |  |  |
| 7. | PWB Assembly Requirements |  |  |  |  |  |  |
| 7.1.1 | Materials: Conformal Coating - R7-1 & 2; Fluxes - R7-4 | Yes |  | No |  |  |  |
| 7.1.2.2 | Components: R7-19 through 22 (no piggy –back component mounting allowed) | Yes |  | No |  |  |  |
| 7.1.2.4 | Layout: thermal component placement consideration: R7-33 through 36 | Yes |  | No |  |  |  |
| 7.1.2.6 | Layout: component lead forms: R7-48 through 52 | Yes |  | No |  |  |  |
| 7.1.3 | # Manufacturing |  |  |  |  |  |  |
| 7.1.3.3/4 | Soldering/Soldering: R7-84 through R7-95 | Yes |  | No |  |  |  |
| 7.1.3.5 | Warpage: R7-96 | Yes |  | No |  |  |  |
| 7.1.3.6 | Solder masks: R7-97 through R7-99 | Yes |  | No |  |  |  |
| 7.1.3.7 | Conformal coatings: R7-100 | Yes |  | No |  |  |  |
| 7.1.3.13 | Repair of PWB assemblies: Component removal and replacement: R7-117 through 126 | Yes |  | No |  |  |  |
| 7.1.3.17 | Modification to PWB: Wire routing - R7-138 through 142 | Yes |  | No |  |  |  |
| 7.1.3.19 | Modification to PWB: Soldering of modification wires – R7-148 (Prototype board assemblies, with plans to re-spin, and containing not more than five wires, may be temporarily permissible for a period not exceeding 6 months.) & R7-149 through 151 | Yes |  | No |  |  |  |
| 8. | Equipment Sub-Assembly and Assembly Requirements |  |  |  |  |  |  |
| 8.1.3 (a) | Design: Accumulation of dust on telecommunication products can provide the potential for electrical breakdown: R7-6 through 10 | Yes |  | No |  |  |  |
| 8.1.3 (b) | Design: Fan or blower cooled equipment shall be fitted with suitable filters - R8-3 through 8 | Yes |  | No |  |  |  |
| 8.1.3 (c) | Design: ESD protective measures during equipment assembly maintenance - R8-23 | Yes |  | No |  |  |  |
| 8.1.3 (d) | Design: Contact breakers and other service-affecting switches shall be so designed as to minimize the risk of accidental activation during routine maintenance and operation. R8-25 | Yes |  | No |  |  |  |
| 9. | # Electrostatic Discharge |  |  |  |  |  |  |
| 9.4.2 | # Circuit Pack ESD Considerations: |  |  |  |  |  |  |
| 9.4.2.2 | Susceptibility – R9-1 through 2 | Yes |  | No |  |  |  |
| 9.4.2.3 | Performance Criteria: R9-3 | Yes |  | No |  |  |  |
| 9.4.2.4 | Specifications: R9-4 through 7 | Yes |  | No |  |  |  |
| 9.5.1 | ESD Caution Labels: R9-19 | Yes |  | No |  |  |  |
| 10. | Product identification & marking requirements: R10-1 & R10-4 through 7 | Yes |  | No |  |  |  |
| 11. | Package requirements: R11-1 through 10 | Yes |  | No |  |  |  |
| 12. | Repair and modification of customer return units: R12-1 through 8 | Yes |  | No |  |  |  |
| 12.2 | Marking: R12-9 | Yes |  | No |  |  |  |
| 12.3 | Repairs: PCB charring - R12-10 through 14 | Yes |  | No |  |  |  |
| 13 | Qualification test: Fluxes requirement R13-1 | Yes |  | No |  |  |  |
| Comments: |  |  |  |  |  |  |  |

H. NEBS TEST RESULTS:

For each Requirement below mark one box (left side) as Not Tested, Partially Conforms, Does not Conform, or Conforms.  Use “Comments” to provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.

H.1.    Spatial Requirements  (Required for CLEC & Carrier Applications)

GR-63, Section 2:	Specifies requirements for physical size of equipment framework, floor loading, line-up, aisle spacing, operations systems, cabling and cable entrance, front/rear access.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.2.    Thermal Requirements   (Required for CLEC & Carrier Applications)

GR-63, Section 4.1 and various (e.g. GR-418, GR-2834, GR-2836):  Specifies temperature, humidity, and altitude range for a controlled or uncontrolled (“hardened”) environments throughout which the equipment must be able to remain operable, and function normally.  Test procedures and criteria vary depending on whether the equipment is being tested for indoor or outdoor installation.  Check Appendix A and the applicable carrier’s clarification document for specific testing requirements.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.3.    Fire Resistance Requirements  (Required for CLEC & Carrier Applications)

GR63, Section 4 or ANSI T.319: Limits frequency of fires and extent of damage due to the materials used, overheating, short-circuit damage, rate of flame spread, secondary fires from dripping flaming/molten material and smoke corrosivity.  The tests measure fire resistance by observing self-extinguish ability and flame spread of a burning unit.  The equipment’s fire hazard is characterized by measuring the radiant heat flux and heat release. Fire resistance estimates are less desirable than actual tests.  Check Appendix A and the applicable carrier’s clarification document for specific testing requirements.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.4.    Handling and Transportation Requirements (Required for Carrier Applications)

GR63, Section 4.3:	Ensures that equipment can be shipped without damage and arrives in serviceable condition.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.5.    Earthquake and Office Vibration Requirements  (CLEC - Earthquake only & Carrier Applications - All)

GR-63, Section 4.4:	 Ensures that seismic or building vibrations from adjacent construction, highways, etc., do not cause operational or performance problems. Nearby heavy machinery, heavy construction, heavy industrial equipment, truck/train traffic, building HVAC systems, or standby generators can result in low frequency vibration.  It is important to know if such low frequency vibration will cause long-term troubles such as connectors becoming loose, or short-term problems like disk drive crashes.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Earthquake Zone: |  |  |  | (Specify the Earthquake Zone that was tested.) |  |  |  |  |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.6.    Airborne Contamination (Required for Carrier Applications)

GR-63, Section 4.5: Describes air quality (particulate) conditions under which equipment is expected to operate properly.  Particulate contamination, specifically soluble salts, can combine with water vapor and result in increased corrosion levels.  Organic vapors and reactive gases can aggravate corrosive actions and can affect disk drive and magnetic tape reliability. Hygroscopic dust contamination creates the potential for resultant intermittent or erratic performance.  Test procedures and criteria vary depending on whether the equipment is being tested for indoor or outdoor installation.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.7.    Acoustic Noise Requirements  (Required for CLEC & Carrier Applications)

GR-63, Section 4.6: Limits noise levels than can emanate from equipment.  This requirement is intended to ensure that OSHA limits are not exceeded.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.8.    Illumination Requirements (Required for Carrier Applications)

GR-63, Section 4.7:  Establishes requirements for surface reflectance and color intended to minimize reflected glare. It is intended to determine the readability of the stenciling and markings on the equipment, under the ambient light level normally encountered in CO equipment space. Surface finishes and colors, marking colors, styles, size shall be clear and of high contrast and low glare. This requirement does not refer to lighting fixtures supplied or ambient light levels generated by the equipment.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.9.    ESD and EFT Immunity Requirements (Required for Carrier Applications)

GR-1089, Section 2:  Ensures that equipment operation is not susceptible to ESD and EFT when normally accepted precautions are used.  The requirement is to do the tests.  The objective is to pass the test.  Lab test reports MUST specifically describe equipment functionality during the test discharges.  ANY abnormal or unexpected behavior or system degradation MUST be described.  Emphasis will be placed on the degree of service degradation.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.10.    EMI Emission Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 3.2:  Ensures that equipment does not emit excessive radiated or conducted emissions that could interfere with the proper operation of other equipment. Lab test reports must clearly show the emissions from the equipment, plotted against the acceptable GR-1089 limits, with the ambient background measurements overlaid on the graph.  Graphs shall be color coded for clarity.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

| Are external ferrites required for EMI Emission compliance? (Yes/No) |  |
| --- | --- |

H.11.    EMI Immunity Requirements (Required Carrier Applications)

GR-1089, Section 3.3:	Ensures that the equipment functions properly and that operation is not susceptible to radiated or conducted emissions from other equipment.  Lab test reports MUST specifically describe equipment functionality during the test.  ANY abnormal or unexpected behavior or system degradation MUST be described.  Emphasis will be placed on the degree of service degradation.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

| Are external ferrites required for EMI Immunity compliance? (Yes/No) |  |
| --- | --- |

H.12.    Lightning and AC Power Fault Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 4:	Prevents or safely limits trouble when equipment is exposed to abnormal or fault conditions resulting from lightning surges and AC power fault conditions that may occur at network terminations.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.13.    Steady-State Power Induction Requirements (Required for Carrier Applications)

GR-1089, Section 5:	Establishes requirements for equipment tolerance of induced, longitudinal (common mode) noise that may be experienced in telephone outside plant facilities.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.14.    DC Potential Difference Requirements (Required for Carrier Applications)

GR-1089, Section 6:	Establishes requirements to ensure that equipment can operate properly when presented with a normally expected potential difference.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.15.    Electrical Safety Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 7:	Ensures that people using or working on or near the equipment are not exposed to hazards.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.16.    Corrosion Requirements (Required for Carrier Applications)

GR-1089, Section 8:	Ensures that a zero or negative potential with respect to ground is maintained to prevent corrosion in outside plant cables when water accidentally enters the cable core.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.17.    Bonding and Grounding Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 9:  Ensures that safe and proper operation of this and other equipment is maintained. If this equipment or any component with a physical or electrical connection to this equipment is to be placed within the switch Isolated Ground Plane, conformance to TR-NWT-000295 (Isolated Ground Plane, Single Point Ground System) is required or Carrier NEBS Compliance approved mitigation measures must be used.  All grounding and bonding conductors must be of sufficient size, as described in TR-NWT-000295 and must use 2-hole crimp lugs based on conductor size.  Reference shall be made to GR-1089 R9-9 for acceptable safety Frame Ground connection.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.18.    Criteria for DC Power Port of Telecommunications Load Equipment  (Required for CLEC & Carrier Applications)

GR-1089, Section 10:  Establishes requirements to ensure that equipment can operate properly when presented with a normally expected DC Power conditions that may occur on the Ports of the Load Equipment.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.19.    GR-487 Requirements for Electronic Equipment Cabinets (Required for Carrier application of outdoor cabinets)

GR-487:	Ensures safe and proper operation of telecom equipment to be placed in an outdoor environment.  The product requires testing to appropriate GR-63 and GR-1089 requirements as directed and augmented by GR-487.

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.20.    Fire Resistance Criteria - Ignitability Requirements (Required for Carrier applications)

### ANSI T1.307-2003:  Fire Resistance Criteria - Ignitability Requirements for Equipment Assemblies, Ancillary Non-Metallic Apparatus, and Fire Spread Requirements for Wire and Cable

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.21.    DC Power Requirements (Required for Carrier Applications)

ANSI T1.315:	Voltage Levels for DC Powered Equipment Used in the Telecommunications Environment

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.22.    Fire Propagation Risk Assessment (Required for CLEC & Carrier Applications)

### ANSI T1.319:	Equipment Assemblies - Fire Propagation Risk Assessment Criteria

| Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.23.    Energy Efficiency (Required for Carrier Applications)

VZ.TPR.9205:	Energy Efficiency Requirements for Telecommunications Equipment (Verizon requirement)

ATIS-0600015.2009 Energy Efficiency for Telecommunications Equipment: Methodology for Measurement and Reporting – General Requirements

| For Verizon Test Facility Name: |  |  |  |  |  |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Report Number: |  |  |  |  |  |  |  | Report Date: |  |  |  |
| Test Results: |  |  |  |  |  |  |  |  |  |  |  |
|  | Not Tested |  |  |  | Partially Conforms |  | Does Not Conform |  |  | Conforms |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |
| For AT&T |  |  |  |  |  |  |  |  |  |  |  |
| Test Facility Name: |  |  |  |  |  |  |  | Test Date: |  |  |  |
| Report Number: |  |  |  |  |  |  |  | Report Date: |  |  |  |
| Test Results: |  |  |  |  |  |  |  |  |  |  |  |
|  | Not Tested |  |  |  | Partially Conforms |  | Does Not Conform |  |  | Conforms |  |
| Comments: |  |  |  |  |  |  |  |  |  |  |  |

H.24.    Thermal Modeling, Simulation and Test (Required for Specific Carrier Applications)

VZ.TPR.9208:	Thermal Management Requirements for Improved Energy Efficiency of Telecommunications Equipment (Verizon Requirement)

| For Verizon Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

H.25.    Lead-Free Solder (Required for Carrier Applications)

VZ.TPR.9307:	Qualification Requirments for Printed Board Assemblies Manufactured with Lead-Free Solder for use in Telecommunications Equipment (Verizon Requirement)

ATIS-0600019.2009 – Test Requirements for Pb-Free Subassemblies

| For Verizon Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

| For AT&T Test Facility Name: |  | Test Date: |  |
| --- | --- | --- | --- |
| Report Number: |  | Report Date: |  |

| Test Results: |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Not Tested |  |  | Partially Conforms |  | Does Not Conform |  | Conforms |
| Comments: |  |  |  |  |  |  |  |  |

Telephony power plants are generally referred to as -48vDC systems.  These plants generally operate (a.k.a. float) at -52v to -54v DC with an equalize mode in some reaching -57v DC. All equipment is expected to operate normally in these ranges and shall operate without faults on a reduced supply voltage as low as -42v DC.  Supply voltages between -48v DC and -42v DC may be encountered during abnormal periods when the battery plant may be in a discharging mode as a result of power failures.